## thresholds type A_B_C_D
Country | A/B | B/C | C/D | Status | Underlying reason for proposed value | Comment
HR | 500 kW | 5 MW | 10 MW | 3 - selected for approval | Alignement with current connection requirements defined in national grid code.

## UE 2016_631_LoRI_TSO (RfG)
Aspect | Non-Exhaustive Requirement | Non-Mandatory Requirement | Article | Definition | Type A | Type B | Type C | Type D | Comment | Implementation in Member State
[10 empty] | AT |  | BA |  | BE |  | BG |  | CH |  | CY |  | CZ |  | DE |  | DK |  | EE |  | ES |  | FI |  | FR |  | GB |  | GR |  | HR | HU |  | IE |  | IS |  | IT |  | LT |  | LU |  | LV |  | ME |  | MK |  | NL |  | NO |  | PL |  | PT |  | RO |  | RS |  | SE |  | SI |  | SK
|  | NA | 7.4 | RSO/TSO | x | x | x | x | Proposal of requirements of general applications | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status
FREQUENCY RELATED PARAMETERS | FREQUENCY RANGES |  | 13.1.a.(i) | TSO | X | X | X | X | time period for operation in the frequency ranges | 47,5-48,5 Hz: 60 min 48,5-49,0 Hz: 60 min 49,0-51,0 Hz unlimited 51,0-51,5 Hz: unlimited | 1 - TSO internal consideration |  |  | Under Coordination: Final values are subject to synchronous CE decision 47,5 Hz – 48,5 Hz: 30 minutes 48,5 Hz – 49,0 Hz: Minimum 60 minutes 49,0 Hz – 51,0 Hz Unlimited | 1 - TSO internal consideration | 47.5Hz - 48.5Hz, ≥ 30 min; 48.5Hz - 49.0Hz, ≥ 30 min; 49.0Hz - 51.0Hz, ∞; 51.0Hz - 51.5Hz, ≥ 30 min | 2a - preliminary: shared with stakeholders, but not publicly available | 30 min | 2a - preliminary: shared with stakeholders, but not publicly available |  |  | 47,5-48,5 Hz: 30 min 48,5-49,0 Hz: 90 min 49,0-51,0 Hz unlimited 51,0-51,5 Hz: unlimited | 2a - preliminary: shared with stakeholders, but not publicly available | 30 min | 2b - preliminary: shared with stakeholders and publicly available | CE: 30 min N: 30 min. |  |  |  | 47.5 - 48.5 Hz--> 30 mins; 48.5 - 49 Hz--> continious; relaxation for U-f deviations simultaneously | 2b - preliminary: shared with stakeholders and publicly available | 30 min | 2a - preliminary: shared with stakeholders, but not publicly available | 30 min | 2 - preliminary shared with stakeholders |  |  |  |  | 47.5Hz - 48.5Hz, ≥ 30 min; 48.5Hz - 49.0Hz, ≥ 60 min; 49.0Hz - 51.0Hz, unlimited; 51.0Hz - 51.5Hz, ≥ 30 min |  |  | 48.5 Hz – 49.0 Hz 90 minutes | 1 - TSO internal consideration | [6 empty] | 30 min | 1 - TSO internal consideration | [6 empty] | Waiting for European coordination | 0 - no consideration | 30 min | 3 - selected for approval | 47,5 Hz–48,5 Hz 30 min. 48,5 Hz–49,0 Hz 30 min | 1 - TSO internal consideration |  |  | 47,5 Hz – 48,5 Hz - minim 30 min 48,5 Hz – 51,0 Hz - minim 30 min 51,0 Hz – 51,5 Hz - 30 minutes | 3 - selected for approval |  |  |  |  | Waiting for European coordination | 0 - no consideration | 47,5-48,5 Hz: 30 min 48,5-49 Hz; 30 min 49 - 51 Hz; Unlimited 51 - 51,5Hz; 30 min | 1 - TSO internal consideration
Continental Europe 47.5 - 48.5 Hz and 48.5 - 49 Hz
Nordic:48.5 - 49 Hz
GB:48.5 - 49 Hz
Ireland:48.5 - 49 Hz
Baltic: 47.5 - 48.5 Hz and 48.5 - 49 Hz and 51 - 51,5 Hz
| RATE OF CHANGE OF FREQUENCY (ROCOF) WITHSTAND CAPABILITY |  | 13.1.(b) | TSO | X | X | X | X | maximum ROCOF for which the Power Generating Module (PGM) shall stay connected | 2 Hz/s | 1 - TSO internal consideration |  |  | 2 Hz/s 500 ms measuring window | 1 - TSO internal consideration | Under discussion | 1 - TSO internal consideration | 2 Hz/s | 1 - TSO internal consideration |  |  | 2 Hz/s | 1 - TSO internal consideration | 2 Hz/s | 1 - TSO internal consideration | (+/- ) 2,5 Hz/s |  |  |  | 2 Hz/s measured in a rolling window of 500 ms | 2b - preliminary: shared with stakeholders and publicly available | 2 Hz/s | 1 - TSO internal consideration |  | 0 - no consideration |  |  |  |  | between 1 Hz/s and 2 Hz/s, measuring window 500 mHz |  |  | 1 Hz/Sec over 500mS window | 1 - TSO internal consideration | [6 empty] | 2.5 | 1 - TSO internal consideration | [6 empty] | Waiting for European coordination | 0 - no consideration | 1,5 Hz/s | 1 - TSO internal consideration | 2,5 Hz/s | 1 - TSO internal consideration |  |  | 1 Hz/sec SG & 2 Hz/s MG | 3 - selected for approval |  |  |  |  | Waiting for European coordination | 0 - no consideration | 2Hz/s | 1 - TSO internal consideration
|  |  |  | RSO TSO | X | X | X | X | specify ROCOF of the loss of main protection |  | 1 - TSO internal consideration |  |  | For loss of main DSO are still investigating alternatives | 1 - TSO internal consideration | Under discussion | 1 - TSO internal consideration | to be defined project-specific |  |  |  | to be discussed | 0 - no consideration | to be defined project-specific |  | to be defined later |  |  |  | n/a |  |  |  | to be defined project-specific | [5 empty] | to be defined project-specific |  |  | 1 Hz/Sec over 500mS window | 1 - TSO internal consideration | [6 empty] | to be defined project-specific | [7 empty] | Waiting for European coordination | 0 - no consideration |  | 0 - no consideration | to be defined project-specific | 1 - TSO internal consideration |  |  | No RSO proposal | 3 - selected for approval |  |  |  |  | Waiting for European coordination | 0 - no consideration
| LIMITED FREQUENCY SENSITIVE MODE (LFSM) |  | 13.2.(a) | TSO | X | X | X | X | frequency threshold and droop settings | Threshold: 50,2 Hz Droop: 5 % | 1 - TSO internal consideration |  |  | Under Coordination: Final values are subject to synchronous CE decision Threshold: 50,2 Hz Droop to be identified at synchronous level | 1 - TSO internal consideration | Type A 50.3 Hz ≤ 2 sec, type B, C and D - adjustable range (50.2 - 50.5 Hz) default 50.3 Hz, 2-12 % default 4.5% | 2a - preliminary: shared with stakeholders, but not publicly available | adjustable ranges for frequency threshold and droop; default values: 50,2 Hz and 5% | 2a - preliminary: shared with stakeholders, but not publicly available |  |  | Threshold: 50,2 Hz Droop: 5 % | 2a - preliminary: shared with stakeholders, but not publicly available | adjustable ranges for frequency threshold and droop; default values: 50,2 Hz and 5% | 2b - preliminary: shared with stakeholders and publicly available | CE FTH:50,2 Hz Droop: 5% N FTH:50,5 Hz Droop: 4% |  |  |  | 50.2 Hz and 5% | 2b - preliminary: shared with stakeholders and publicly available | 50,5 Hz Range: 2- 12 % | 1 - TSO internal consideration | adjustable ranges for frequency threshold and droop; default values: 50,2 Hz and 3% | 2 - preliminary shared with stakeholders |  |  |  |  | Threshold: 50,2 Hz Droop: adjustable 2 % - 12 %; default 5 % |  |  | Site - specific sets the functional capability of response - however 50.2 Hz activation Droop 4% | 1 - TSO internal consideration | [6 empty] | adjustable ranges for frequency threshold and droop; default values: 50,2 Hz and 5% | 1 - TSO internal consideration | [6 empty] | Waiting for European coordination | 0 - no consideration | 50,2-50,5 Hz (Entire range should be available, actual setting decided by other regulation) | 1 - TSO internal consideration | adjustable ranges for frequency threshold and droop within the ranges specified in NC RfG | 1 - TSO internal consideration |  |  | 50,2 Hz and droop settings shall be between (2-12)% | 3 - selected for approval |  |  |  |  | Waiting for European coordination | 0 - no consideration | Threshold 50,2 Hz Droop 5% | 1 - TSO internal consideration
|  | X |  | TSO | X | X | X | X | requirements in case of expected compliance on an aggregate level |  | 1 - TSO internal consideration |  |  | Site specific | 1 - TSO internal consideration | n/a |  |  | 1 - TSO internal consideration |  |  |  |  | n/a to type D PGMs |  | 13.2.b.: n/a |  |  |  | n/a |  |  |  | n/a | [8 empty] | Same - 50.2 Hz activation Droop 4% | 1 - TSO internal consideration | [7 empty] | 1 - TSO internal consideration | [6 empty] | Waiting for European coordination | 0 - no consideration |  |  | n/a | [9 empty] | Waiting for European coordination | 0 - no consideration |  | 0 - no consideration
|  | X | 13.2.e | TSO | X | X | X | X | expected behaviour of the PGM once the minimum regulating level is reached | continuous operation | 1 - TSO internal consideration |  |  | Should remain at minimum level | 1 - TSO internal consideration | n/a |  | continuous operation | 1 - TSO internal consideration |  |  | continuous operation | 1 - TSO internal consideration | to continue operation at this level | 2b - preliminary: shared with stakeholders and publicly available | 13.2.f.i. continue operation at this level | [5 empty] | 13.2.f.i. continue operation at this level | 1 - TSO internal consideration | to continue operation at this level or to continue decreasing power (depending on technical capabilities) | 2 - preliminary shared with stakeholders |  |  |  |  | sync. PGM to continue operation at this level; PPM: to continue decreasing power; disconnection for both at 51,5 Hz |  |  | Continous operation at min level | 1 - TSO internal consideration | [6 empty] | continous operation | 1 - TSO internal consideration | [6 empty] | Waiting for European coordination | 0 - no consideration | Disconnection | 1 - TSO internal consideration | to continue operation at this level | 1 - TSO internal consideration |  |  | disconnection at 51,5 Hz | 3 - selected for approval |  |  |  |  | Waiting for European coordination | 0 - no consideration | Continuing operation at minimal level | 1 - TSO internal consideration
| ADMISSIBLE ACTIVE POWER REDUCTION FROM MAXIMUM OUTPUT WITH FALLING FREQUENCY |  | 13.4 | TSO | X | X | X | X | admissible active power reduction from maximum output with falling frequency | 10%Pmax/Hz starting at 49,5 Hz | 1 - TSO internal consideration |  |  | Under Coordination: Final values are subject to synchronous CE decision Frequency reduction below 49 Hz in a way that at 47,5 Hz maximum power shall not be lower than 95% of the maximum capacity . For CCGT units the above requirement shall be retained for a period of 5 min at least subsequently to 49 Hz. | 1 - TSO internal consideration | 49.0Hz, 0% ÷ 5% default (0%); 48.5Hz, 1% ÷ 10% default (6%); 48.0Hz, 2% ÷ 15% default (9%); 47.5Hz, 3% ÷ 20% default (12%) | 2a - preliminary: shared with stakeholders, but not publicly available | 10%Pmax/Hz starting at 49,5 Hz | 2a - preliminary: shared with stakeholders, but not publicly available |  |  | Between 49-50 Hz: 0 % Below 49 Hz: 2% of Pmax per Hz | 1 - TSO internal consideration | 10%Pmax/Hz starting at 49,5 Hz | 2b - preliminary: shared with stakeholders and publicly available | to be defined |  |  |  | curve crossing at 49.5 Hz and with a slope of 10% | 2b - preliminary: shared with stakeholders and publicly available | below 49 Hz, 10 % per Hz | 1 - TSO internal consideration | 10%Pmax/Hz starting at f1 ≤ 49,5 Hz (f1 is depending on technical limitation) | 2 - preliminary shared with stakeholders |  |  |  |  | Between 49-50 Hz: 0 % Below 49 Hz: 6,67% of Pmax per Hz |  |  | 2% reduction starting from 49.5Hz | 1 - TSO internal consideration | [6 empty] | 10%Pmax/Hz starting at 49,5 Hz | 1 - TSO internal consideration | [6 empty] | Waiting for European coordination | 0 - no consideration | 49,5 Hz/10% | 3 - selected for approval | Sync. PGM - 10%Pmax/Hz starting at 49,0 Hz CCGT-10%Pmax/Hz starting at 49,5 Hz and 4%Pmax/Hz starting at 49,0 Hz PPM- 2% starting at 49Hz | 1 - TSO internal consideration |  |  | In cases argue by the technical data (a) Between 48-49 Hz falling by a reduction rate of 2 % of the nominal capacity at 50 Hz per 1 Hz frequency drop. (b) below 49,5 Hz falling by a reduction rate of 10 % of the maximum capacity at 50 Hz per 1 Hz frequency drop. | 3 - selected for approval |  |  |  |  | Waiting for European coordination | 0 - no consideration | Reduction 10% of Pmax per Hz staring at 49,5 Hz | 1 - TSO internal consideration
|  |  | 13.5 | TSO | X | X | X | X | definition of the ambient conditions applicable when defining the admissible active power reduction |  | 0 - no consideration |  |  | Under Coordination: Final values are subject to synchronous CE decision The ambient conditions considered are the nominal ones as per the design conditions | 1 - TSO internal consideration | Awaiting proposals from owners |  | PGM owner to provide information to the network operator for approval | 2a - preliminary: shared with stakeholders, but not publicly available |  |  |  |  | PGM owner to provide information to the network operator for approval | 2b - preliminary: shared with stakeholders and publicly available | to be defined |  |  |  | curve defined at ambient temperature: 25 º | 2b - preliminary: shared with stakeholders and publicly available | ambient temperature, where dimensioned P production available | 1 - TSO internal consideration | defining ambiant conditions applicable to be done ( probably 2 temperatures) | 2 - preliminary shared with stakeholders |  |  |  |  | has not been considered yet |  |  | This shall be the value at 10°C, 70 % relative humidity and 1013 hPa. | 1 - TSO internal consideration | [7 empty] | 0 - no consideration | [6 empty] | Waiting for European coordination | 0 - no consideration | Case specific | 3 - selected for approval | Active power reduction with falling frequency is specified for niminal ambient conditions, in principle. PGM owner to provide information to the network operator regarding corelation between ambient conditions vs admissible active power maximum output | 1 - TSO internal consideration |  |  |  | 3 - selected for approval |  |  |  |  | Waiting for European coordination | 0 - no consideration
| FREQUENCY STABILITY |  | 15.2.(a) | TSO |  | X | X | X | time period for frequency stability to be reached | Inverter-connected generators shall reach the new setpoint within 1 minute Synchronous generators shall reach the new setpoint within 5 minutes tolerance level = +/- 5 % of nominal power | 1 - TSO internal consideration |  |  | Site Specific requirements |  | to be defined |  | to be defined project-specific | 1 - TSO internal consideration |  |  |  |  | to be defined project-specific |  | 10 sec |  |  |  | 15 min | 2b - preliminary: shared with stakeholders and publicly available | tbd |  | to be defined project-specific | [5 empty] | PGM: The time period depends on the technology, generators set point at the time of instruction and defined minimum rates of active power change (2 % Pr/min for TPP and 1 % Pr/sec for HPP); PPM: time of response is 1 minute; The tolerance: 1 % Pn - 5 % Pn |  |  | to be specified on a site specific basis. | 1 - TSO internal consideration | [6 empty] | to be defined project-specific | 1 - TSO internal consideration | [6 empty] | Waiting for European coordination | 0 - no consideration | Hydro: 40%/min Gas: 10-20%/min Power park modules; 200%/min Others; 4%/min | 2a - preliminary: shared with stakeholders, but not publicly available | 15 min with 1% tolerance | 1 - TSO internal consideration |  |  | The time period within which the adjusted active power setpoint must be reached or the rate of change of active power to the modification ot the reference is 2-10% Pn / min depending on the technology, the dead time (the time of the prime mover resource) is 2 seconds, and the tolerance to achieve reference is 1% Pn | 3 - selected for approval |  |  |  |  | Waiting for European coordination | 0 - no consideration | project specific req. | 1 - TSO internal consideration
| LFSM-U |  | 15.2.c | TSO |  |  | X | X | definition of the frequency threshold and droop | Threshold: 49,8 Hz Droop: 5 % | 1 - TSO internal consideration |  |  | Under Coordination: Final values are subject to synchronous CE decision Deadband: 200 mHz Capable of adjusting slope between 2 and 12 % / Initial setting to be defined Site Specific Activation delay less than 2s if not possible technical justification is needed | 1 - TSO internal consideration | Adjustable range 49,5Hz to 49,8Hzb (stanfart 49,7Hz), 5%. | 2a - preliminary: shared with stakeholders, but not publicly available | adjustable ranges for frequency threshold and droop; default values: 49,8 Hz and 5% | 1 - TSO internal consideration |  |  | Threshold: 49,8 Hz Droop: 5 % | 1 - TSO internal consideration | adjustable ranges for frequency threshold and droop; default values: 49,8 Hz and 5% |  | to be defined |  |  |  | 49.8 Hz and 5% of droop | 2b - preliminary: shared with stakeholders and publicly available | 49.5 Hz Range: 2- 12 % | 1 - TSO internal consideration | adjustable ranges for frequency threshold and droop; default values: 49,8 Hz and droop tbd | 2 - preliminary shared with stakeholders |  |  |  |  | Threshold: 49,8 Hz Droop: adjustable between 2 % - 12 % (default 5 %) |  |  | Site - specific sets the functional capability of response - however setting likely to be 49.5 Hz activation Droop 4% | 1 - TSO internal consideration | [6 empty] | adjustable ranges for frequency threshold and droop; default values: 49,8 Hz and droop tbd | 1 - TSO internal consideration | [6 empty] | Waiting for European coordination | 0 - no consideration | 49,5-49,8 Hz (Entire range should be available, actual setting decided by other regulation) | 1 - TSO internal consideration | adjustable ranges for frequency threshold and droop within the ranges specified in NC RfG | 1 - TSO internal consideration |  |  | 49,8 Hz and the droop in the limits of (2-12)% | 3 - selected for approval |  |  |  |  | Waiting for European coordination | 0 - no consideration | Threshold:49,8Hz Droop: 5% | 1 - TSO internal consideration
|  |  |  | TSO |  |  | X | X | definition of Pref | - sync. PGM: Pref = Pmax - PPM: Pref = Pact at overfrequency | 1 - TSO internal consideration |  |  | Pref is Pmax for Synchronous power generating module and Maximum capacity for PPM | 1 - TSO internal consideration | Pref=Pmax | 2a - preliminary: shared with stakeholders, but not publicly available | rated capacity | 1 - TSO internal consideration |  |  | - sync. PGM: Pref = Pmax - PPM: Pref = Pact at overfrequency | 1 - TSO internal consideration | - sync. PGM: Pref = Pmax - PPM: Pref = Pact at overfrequency | 2b - preliminary: shared with stakeholders and publicly available | PGM: Pref = Pmax PPM: |  |  |  | Pmax | 2b - preliminary: shared with stakeholders and publicly available | Pmax | 1 - TSO internal consideration | - sync. PGM: Pref = Pmax - PPM: Pref = Pact at overfrequency | 2 - preliminary shared with stakeholders |  |  |  |  | - sync. PGM: Pref = Pmax - PPM: Pref = Pavailable at f≥50Hz |  |  | Should this be in a spreadsheet? | 1 - TSO internal consideration | [6 empty] | to be confirmed | 1 - TSO internal consideration | [6 empty] | Waiting for European coordination | 0 - no consideration | Pref = Pmax | 1 - TSO internal consideration | - sync. PGM: Pref = Pmax - PPM: Pref = Pmax | 1 - TSO internal consideration |  |  | Pref - maximum capacity | 3 - selected for approval |  |  |  |  | Waiting for European coordination | 0 - no consideration | Pref=Pmax | 1 - TSO internal consideration
| FREQUENCY SENSITIVE MODE |  | 15.2.d.(i) | TSO |  |  | X | X | parameters of the Frequency Sensitive Mode (FSM): | Already defined in APG's prequalification documents; mainly textual adaptions necessary | 1 - TSO internal consideration |  |  | Defined in Elia's prequalification requirements | 2b - preliminary: shared with stakeholders and publicly available |  |  | Already defined in the prequalification documents; mainly textual adaptions necessary | 1 - TSO internal consideration | [39 empty] | Waiting for European coordination | 0 - no consideration |  |  |  | 1 - TSO internal consideration | [8 empty] | Waiting for European coordination | 0 - no consideration
[9 empty] | - active Power range related to Maximum capacity | Already defined in APG's prequalification documents; mainly textual adaptions necessary | 1 - TSO internal consideration |  |  | ≥ 2 % | 2b - preliminary: shared with stakeholders and publicly available | ≤5% | 2a - preliminary: shared with stakeholders, but not publicly available | Already defined in the prequalification documents; mainly textual adaptions necessary | 1 - TSO internal consideration |  |  | keep a range 1.5-10% | 1 - TSO internal consideration | 2% | 2b - preliminary: shared with stakeholders and publicly available | keep a range 1.5-10% |  |  |  | adjustable from 1.5% to 10% | 2b - preliminary: shared with stakeholders and publicly available | ≥5 % depending on primary energy source (TBD) | 1 - TSO internal consideration | ≥2.5% | 2 - preliminary shared with stakeholders |  |  |  |  | ≥ 2 % |  |  | 10% | 1 - TSO internal consideration | [14 empty] | Waiting for European coordination | 0 - no consideration | 5% | 1 - TSO internal consideration | 5% | 1 - TSO internal consideration |  |  | (1,5-10)% | 3 - selected for approval |  |  |  |  | Waiting for European coordination | 0 - no consideration | 2% Pmax | 1 - TSO internal consideration
[9 empty] | - frequency response insensitivity | Already defined in APG's prequalification documents; mainly textual adaptions necessary | 1 - TSO internal consideration |  |  | ¦deltaf1 ¦ maximum is 10 mHz & ¦deltaf1 ¦/fn maximum 0,02% | 2b - preliminary: shared with stakeholders and publicly available | 10 mHz | 2a - preliminary: shared with stakeholders, but not publicly available | Already defined in the prequalification documents; mainly textual adaptions necessary | 1 - TSO internal consideration |  |  | 10 mHz | 1 - TSO internal consideration | 10 mHz | 2b - preliminary: shared with stakeholders and publicly available | 10 mHz |  |  |  | 10 mHz | 2b - preliminary: shared with stakeholders and publicly available | 10 mHz | 1 - TSO internal consideration | 10 mHz | 2 - preliminary shared with stakeholders |  |  |  |  | ≤10 mHz |  |  | 10mHz | 1 - TSO internal consideration | [14 empty] | Waiting for European coordination | 0 - no consideration | 10 mHz | 1 - TSO internal consideration | 10 mHz | 1 - TSO internal consideration |  |  | 10 mHz and (0,02-0,06)% | 3 - selected for approval |  |  |  |  | Waiting for European coordination | 0 - no consideration | 0-200mHz | 1 - TSO internal consideration
[9 empty] | - frequency response dead band | Already defined in APG's prequalification documents; mainly textual adaptions necessary | 1 - TSO internal consideration |  |  | 10 mHz if the frequency response insensitivity is 0 0 mHz for an insensitivity of 10 mHz | 2b - preliminary: shared with stakeholders and publicly available | 20 mHz | 2a - preliminary: shared with stakeholders, but not publicly available | Already defined in the prequalification documents; mainly textual adaptions necessary | 1 - TSO internal consideration |  |  | 0-500 mHz | 1 - TSO internal consideration | 0 - 200 mHz | 2b - preliminary: shared with stakeholders and publicly available | 0-500 mHz |  |  |  | 0 | 2b - preliminary: shared with stakeholders and publicly available | range 0 - 500 Hz | 1 - TSO internal consideration | 0 - 200 mHz (0 required if FSM is activated) | 2 - preliminary shared with stakeholders |  |  |  |  | 20 - 200 mHz |  |  | 15mHz | 1 - TSO internal consideration | [14 empty] | Waiting for European coordination | 0 - no consideration | 0-500 mHz (Entire range should be available, actual setting decided by other regulation) | 1 - TSO internal consideration | 0–500 mHz | 1 - TSO internal consideration |  |  | 0 mHz | 3 - selected for approval |  |  |  |  | Waiting for European coordination | 0 - no consideration | 10mHz | 1 - TSO internal consideration
[9 empty] | - droop | Already defined in APG's prequalification documents; mainly textual adaptions necessary | 1 - TSO internal consideration |  |  | Available in a range between 2 and 12 % to be decided specifically by site depending on the selected power range | 2b - preliminary: shared with stakeholders and publicly available | 2-10% | 2a - preliminary: shared with stakeholders, but not publicly available | Already defined in the prequalification documents; mainly textual adaptions necessary | 1 - TSO internal consideration |  |  | selectable 2-12% | 1 - TSO internal consideration | adjustable range 2 - 12% | 2b - preliminary: shared with stakeholders and publicly available | adjustable range 2 - 12% |  |  |  | adjustable from 2% to 12% | 2b - preliminary: shared with stakeholders and publicly available | adjustable from 2% to 12% | 1 - TSO internal consideration | 3-12% (full activation of the active power range reserve within 200 mHz) | 2 - preliminary shared with stakeholders |  |  |  |  | adjustable from 2% to 12% |  |  | 2-10% control system range | 1 - TSO internal consideration | [14 empty] | Waiting for European coordination | 0 - no consideration | 2-12% (Entire range should be available, actual setting decided by other regulation) | 1 - TSO internal consideration | adjustable range 2 - 12% | 1 - TSO internal consideration |  |  | (2-12)% | 3 - selected for approval |  |  |  |  | Waiting for European coordination | 0 - no consideration | 2-12% | 1 - TSO internal consideration
|  |  | 15.2.d.(iii) | TSO |  |  | X | X | maximum admissible full activation time | Already defined in APG's prequalification documents; mainly textual adaptions necessary | 1 - TSO internal consideration |  |  | 30 seconds | 2b - preliminary: shared with stakeholders and publicly available | 30s | 2a - preliminary: shared with stakeholders, but not publicly available | Already defined in the prequalification documents; mainly textual adaptions necessary | 1 - TSO internal consideration |  |  | PGMs = 30 s PPMs =1 s | 1 - TSO internal consideration | 30 s | 2b - preliminary: shared with stakeholders and publicly available | 30 s |  |  |  | for the 10% P/Pref: for PPMs 2 sec; for SGM 12 sec | 2b - preliminary: shared with stakeholders and publicly available | 30 s | 1 - TSO internal consideration | 30 s | 2 - preliminary shared with stakeholders |  |  |  |  | 30 s |  |  | Site-specific | 1 - TSO internal consideration | [14 empty] | Waiting for European coordination | 0 - no consideration | Type C; 9 sec Type D; 5 sec | 1 - TSO internal consideration | 30 s | 1 - TSO internal consideration |  |  | 30 sec | 3 - selected for approval |  |  |  |  | Waiting for European coordination | 0 - no consideration | 30 sec | 1 - TSO internal consideration
|  |  | 15.2.d.(iv) | TSO |  |  | X | X | maximum admissible initial delay for power generating modules with inertia | Already defined in APG's prequalification documents; mainly textual adaptions necessary | 1 - TSO internal consideration |  |  | Maximum admissible time is 2 secondes | 2b - preliminary: shared with stakeholders and publicly available | 2s | 2a - preliminary: shared with stakeholders, but not publicly available | Already defined in the prequalification documents; mainly textual adaptions necessary | 1 - TSO internal consideration |  |  | as short as possible, to be justified if > 2 s | 1 - TSO internal consideration | as short as possible, to be justified if > 2 s | 2b - preliminary: shared with stakeholders and publicly available | to be defined |  |  |  | 2 sec | 2b - preliminary: shared with stakeholders and publicly available | 2 s | 1 - TSO internal consideration | as short as possible, to be justified if > 2 s | 2 - preliminary shared with stakeholders |  |  |  |  | 2 s |  |  | Site-specific | 1 - TSO internal consideration | [14 empty] | Waiting for European coordination | 0 - no consideration | 2 sec (not unreasonably delayed) | 1 - TSO internal consideration | 2 s | 1 - TSO internal consideration |  |  | 2 sec | 3 - selected for approval |  |  |  |  | Waiting for European coordination | 0 - no consideration | 2 sec | 1 - TSO internal consideration
|  | X | 15.2.d.(iv) | TSO |  |  | X | X | maximum admissible initial delay for power generating modules without inertia | Already defined in APG's prequalification documents; mainly textual adaptions necessary | 1 - TSO internal consideration |  |  | Maximum admissible time is 2 secondes | 2b - preliminary: shared with stakeholders and publicly available | 1s | 2a - preliminary: shared with stakeholders, but not publicly available | Already defined in the prequalification documents; mainly textual adaptions necessary | 1 - TSO internal consideration |  |  |  |  | 1 s | 2b - preliminary: shared with stakeholders and publicly available | to be defined |  |  |  | 500 ms | 2b - preliminary: shared with stakeholders and publicly available | 2 s | 1 - TSO internal consideration | as short as possible, to be justified if > 2 s | 2 - preliminary shared with stakeholders |  |  |  |  | 500 ms |  |  | Site speciic | 1 - TSO internal consideration | [14 empty] | Waiting for European coordination | 0 - no consideration | 2 sec (not unreasonably delayed) | 1 - TSO internal consideration | 0,5 s | 1 - TSO internal consideration |  |  | 1 sec | 3 - selected for approval |  |  |  |  | Waiting for European coordination | 0 - no consideration | 2 sec | 1 - TSO internal consideration
|  |  | 15.2.d.(v) | TSO |  |  | X | X | time period for the provision of full active power frequency response | Already defined in APG's prequalification documents; mainly textual adaptions necessary | 1 - TSO internal consideration |  |  | 15 min | 2b - preliminary: shared with stakeholders and publicly available | ≥15 min. | 2a - preliminary: shared with stakeholders, but not publicly available | Already defined in the prequalification documents; mainly textual adaptions necessary | 1 - TSO internal consideration |  |  | > 15 min (other PPs) > 30 min (hydro PPs) | 1 - TSO internal consideration | > 15 min | 2b - preliminary: shared with stakeholders and publicly available | 15 min |  |  |  | at least 15 mins | 2b - preliminary: shared with stakeholders and publicly available | at least 15 mins | 1 - TSO internal consideration | > 15 min | 2 - preliminary shared with stakeholders |  |  |  |  | 15 min |  |  | 20 minutes | 1 - TSO internal consideration | [14 empty] | Waiting for European coordination | 0 - no consideration | 15 minutes | 0 - no consideration | at least 30 min | 1 - TSO internal consideration |  |  | 30 min | 3 - selected for approval |  |  |  |  | Waiting for European coordination | 0 - no consideration | 15 min | 1 - TSO internal consideration
| REAL-TIME MONITORING OF FSM |  | 15.2.g | RSO or TSO |  |  | X | X | list of the necessary data which will be sent in real time | Already defined in APG's prequalification documents; mainly textual adaptions necessary | 1 - TSO internal consideration |  |  | Further monitoring requirements are Defined in Elia's prequalification requirements | 2b - preliminary: shared with stakeholders and publicly available | to be defined |  | only partly available | 1 - TSO internal consideration |  |  |  |  | to be defined project-specific |  | to be defined |  |  |  | in addition to the listed signals, also the measurment the available reserve (downwards and upwards) | 2b - preliminary: shared with stakeholders and publicly available | tbd | 1 - TSO internal consideration | data used by our monitoring tool | 1 - TSO internal consideration |  |  |  |  | Unit status (On/Off); Governor status (On/Off), Governor mode of operation (f/P/other); Frequency droop (%); Frequency droop status (On/Off); Nominal power (MW); Regulation gain (MW/Hz); Dead band-positive limit (Hz), Dead-band-negative limit (Hz); Dead band status (On/Off);Unit upper power limit (MW); Unit lower power limit (MW); Unit active power (MW); Frequency (Hz); Active power reference (MW) |  |  | Site Specific. Grid Code does not inlcude an exhaustive signal list but allows TSO to specify additional signals as necessary. | 1 - TSO internal consideration | [14 empty] | Waiting for European coordination | 0 - no consideration |  | 0 - no consideration | The addtional signals to be in line with existing PSE standards. Depending of the technology TSO have a right to specify extra signals irrespecticve of the standards, as project specifi data. | 1 - TSO internal consideration |  |  |  | 3 - selected for approval |  |  |  |  | Waiting for European coordination | 0 - no consideration | As defined in RfG | 1 - TSO internal consideration
| RATES OF CHANGE OF ACTIVE POWER OUTPUT |  | 15.6.e | RSO TSO |  |  | X | X | definition of the minimum and maximum limits on rates of change of active power output (ramping limits) in both an up and down direction, taking into consideration the specific characteristics of the prime mover technology | Minimum gradient: 5% per minute Maximum gradient: not yet defined 100 % refers to the maximum possible operating range of the generator | 1 - TSO internal consideration |  |  | Site specific requirements | 2b - preliminary: shared with stakeholders and publicly available | to be defined |  | specified within connection agreements | 4 - approved/binding |  |  |  |  | > 4% Pmax/min in case of instructions for system security | 2b - preliminary: shared with stakeholders and publicly available | 20 % of Pn/min |  |  |  | n/a |  | tbd | 1 - TSO internal consideration | PGM owner to provide information to the network operator for approval | 2 - preliminary shared with stakeholders |  |  |  |  | sync. PGM: between 1% Pmax/sec and 2% Pmax/min depending on the technology (thermal, hyrdo); PPM: project specific requirement |  |  | Can be site specific but not less than 1.5 % of maximum capacity. | 1 - TSO internal consideration | [14 empty] | Waiting for European coordination | 0 - no consideration |  | 0 - no consideration | reference values are to be specify by TSO depending on the technology. Binding values to be defined project-specific. | 1 - TSO internal consideration |  |  | rate of change of active power is in the range: 1-20% Pn | 3 - selected for approval |  |  |  |  | Waiting for European coordination | 0 - no consideration | Project specific req. | 1 - TSO internal consideration
VOLTAGE RELATED PARAMETERS | FAULT RIDE THROUGH CAPABILITY |  | 14.3.a | TSO |  | X | X | X | voltage-against-time profile | Further considerations mainly depend on outcomes of an ongoing R&D project | 1 - TSO internal consideration |  |  | 20170201_SGU_Technical_Summary_TFINCs.pdf Page 8 (Type B+C) | 2b – preliminary shared with stakeholders and publicly available | Available from type D |  |  | 1 - TSO internal consideration |  |  |  |  | n/a to type D PGMs |  | Defined only available in PPT. |  |  |  | - sync. PGM: Uret: 0,05 Uclear: 0,7 Urec1: 0,7 Urec2: 0,85 tclear: 0,15 s trec1: 0,15 s trec2: 0,5 s trec3: 1,5 s - PPM: Uret: 0,05 Uclear: 0,05 Urec1: 0,05 Urec2: 0,85 tclear: 0,2 s trec1: 0,2 trec2: 0,2 s trec3: 1,5 s | 2b - preliminary: shared with stakeholders and publicly available | - sync. PGM: Uret: 0,05 Uclear: 0,7 Urec1: 0,7 Urec2: 0,85 tclear: 0,15 s trec1: 0,15 s trec2: 0,7 s trec3: 1,5 s - PPM: Uret: 0,05 Uclear: 0,05 Urec1: 0,05 Urec2: 0,85 tclear: 0,15 s trec1: 0,15 trec2: 0,15 s trec3: 1,5 s | 1 - TSO internal consideration | - sync. PGM: Uret: 0,05 Uclear: 0,7 Urec1: 0,7 Urec2: 0,9 tclear: 0,15 s (0,25 s in specific areas) trec1: 0,15 s (0,25 s) trec2: 0,7 s trec3: 1,5 s - PPM: Uret: 0,05 Uclear: 0,05 Urec1: 0,05 Urec2: 0,85 tclear: 0,15 s (0,25 s in specific areas) trec1: 0,15 s (0,25 s) trec2: 0,15 s (0,25 s) s trec3: 1,5 s | 2 - preliminary shared with stakeholders |  |  |  |  | sync. PGM: Uret: 0,05 Uclear: 0,7 Urec1: 0,7 Urec2: 0,9 tclear: 0,15 s trec1: 0,15 s trec2: 0,7 s trec3: 1,5 s PPM: Uret: 0,05 Uclear: 0,15 Urec1: 0,15 Urec2: 0,85 tclear: 0,15 s trec1: 0,15 s trec2: 0,15 s trec3: 1,5 s |  |  | Uret: 0.05pu tclear: 150mS Uclear: 0.7pu trec1: 150mS Urec1: 0.7pu trec2: 450mS Urec2: 0.9pu trec3: 450mS | 1 - TSO internal consideration | [14 empty] | Synchronous Generators Uret: 0.05pu tclear: 150ms Uclear: 0.7pu trec1: 150ms Urec1: 0.7pu trec2: 300ms Urec2: 0.85pu trec3: 1,5 s PPM Uret: 0.05pu tclear: 250ms Uclear: 0.05pu trec1: 250ms Urec1: 0.05pu trec2: 250ms Urec2: 0.85pu trec3: 3,0 s | 1 - TSO internal consideration | Synchronous Generators Uret: 0.3pu tclear: 150ms Uclear: 0.7pu trec1: 150ms Urec1: 0.7pu trec2: 150ms Urec2: 0.9pu trec3: 1 s PPM Uret: 0.15pu tclear: 150ms Uclear: 0.15pu trec1: 150ms Urec1: 0.15pu trec2: 150ms Urec2: 0.9 pu trec3: 1,5 s | 2a - preliminary: shared with stakeholders, but not publicly available | sync. PGMs: Uret: 0,05 tclear: 0,15 Uclear: 0,7 trec1: 0,15 Urec1: 0,7 trec2: 0,7 Urec2: 0,85 trec3: 1,5 Tabela 3.2 PPMs: Uret: 0,05 tclear: 0,15 Uclear: 0,05 trec1: 0,15 Urec1: 0,05 trec2: 0,15 Urec2: 0,85 trec3: 2,50 | 1 - TSO internal consideration |  |  |  | 3 - selected for approval |  |  |  |  | studies undergoing | 1 - TSO internal consideration | Synchronous Generators Uret: 0.05pu tclear: 250ms Uclear: 0.7pu trec1: 250ms Urec1: 0.7pu trec2: 250ms Urec2: 0.85pu trec3: 1,5 s PPM Uret: 0.05pu tclear: 250ms Uclear: 0.05pu trec1: 250ms Urec1: 0.05pu trec2: 250ms Urec2: 0.85pu trec3: 1,5 s | 1 - TSO internal consideration
|  |  | 14.3.b | TSO |  | X | X | X | voltage-against-time profile for asymmetric faults | Further considerations mainly depend on outcomes of an ongoing R&D project | 1 - TSO internal consideration |  |  | The diagram for FRT capability for type B andC PGM to withstand asymetric faults will be identical with the one requested to be witstand for symetric one. | 2b – preliminary shared with stakeholders and publicly available | Available from type D |  |  | 1 - TSO internal consideration |  |  |  |  | n/a to type D PGMs |  | Defined only available in PPT. |  |  |  |  | 2b - preliminary: shared with stakeholders and publicly available |  |  |  | 2 - preliminary shared with stakeholders |  |  |  |  | no difference between symetric and asymetric faults |  |  | Same as 14.3.a | 1 - TSO internal consideration | [14 empty] | Identical to symmetrical faults | 1 - TSO internal consideration | Identical | 0 - no consideration | the same profile as for symetric faults, see above | 1 - TSO internal consideration |  |  | fault-ride-through capabilities in case of asymmetrical faults shall stay identical with the form and with the defined parameters for symmetrical faults | 3 - selected for approval |  |  |  |  | studies undergoing | 1 - TSO internal consideration | As for symmetrical fault | 1 - TSO internal consideration
|  |  | 16.3.a.(i) | TSO |  |  |  | X | voltage-against-time profile | Further considerations mainly depend on outcomes of an ongoing R&D project | 1 - TSO internal consideration |  |  | 20170201_SGU_Technical_Summary_TFINCs.pdf (page 19 SPGM type D) In accordance with Request for Generators Connection Code U= 1 pu represents the rated voltage (phase-to-phase) at the connection point. | 2b - preliminary: shared with stakeholders and publicly available | PPM U≥0 t ≤0.15s; U≥0.25 t≤0.7s; U≥0.5 t≤1s; U≥0.85 t≤1.5s SYNC U ≥0 t ≤0.15s; U ≥0.4 t ≤0.45s; U ≥0.5 t ≤0.7s; U ≥0.85 t ≤1.5s | 2a - preliminary: shared with stakeholders, but not publicly available |  | 1 - TSO internal consideration |  |  |  |  | - sync. PGM: Uret: 0 Uclear: 0,25 Urec1: 0,7 Urec2: 0,85 tclear: 0,15 s trec1: 0,3 s trec2: 0,5 s trec3: 3 s - PPM: Uret: 0 Uclear: 0 Urec1: 0 Urec2: 0,85 tclear: 0,15 s trec1: 0,15 s trec2: 0,15 s trec3: 3 s | 2b - preliminary: shared with stakeholders and publicly available | Defined only available in PPT. |  |  |  | - sync. PGM: Uret: 0,0 Uclear: 0,27 Urec1: 0,7 Urec2: 0,85 tclear: 0,15 s trec1:0,25 s trec2: 0,5 s trec3: 1,5 s - PPM: Uret: 0 Uclear: 0 Urec1: 0 Urec2: 0,85 tclear: 0,15 s trec1: 0,15 s trec2: 0,15 s trec3: 1,5 s | 2b - preliminary: shared with stakeholders and publicly available | - sync. PGM: Uret: 0,0 Uclear: 0,25 Urec1: 0,55 Urec2: 0,85 tclear: 0,20 s trec1:0,4 s trec2: 0,7 s trec3: 1,0 s - PPM: Uret: 0 Uclear: 0 Urec1: 0 Urec2: 0,85 tclear: 0,2 s trec1: 0,2 s trec2: 0,2 s trec3: 1,5 s | 1 - TSO internal consideration | - sync. PGM: Uret: 0,05 Uclear: 0,5 Urec1: 0,5 Urec2: 0,9 tclear: 0,15 s (0,25 s in specific areas) trec1:0,15 s (0,25 s) trec2: 0,7 s trec3: 1,35 s - PPM: Uret: 0 Uclear: 0 Urec1: 0 Urec2: 0,85 tclear: 0,15 s (0,25 s in specific areas) trec1: 0,15 s (0,25 s) trec2: 0,15 s (0,25 s) s trec3: 1,5 s | 2 - preliminary shared with stakeholders |  |  |  |  | - sync. PGM: Uret: 0 Uclear: 0,25 Urec1: 0,5 Urec2: 0,9 tclear: 0,15 s trec1: 0,15 s trec2: 0,7 s trec3: 1,5 s - PPM: Uret: 0 Uclear: 0 Urec1: 0 Urec2: 0,85 tclear: 0,15 s trec1: 0,15 s trec2: 0,15 s trec3: 1,5 s |  |  | Synchronous Generators Uret: 0pu tclear: 150mS Uclear: 0.25pu trec1: 150mS Urec1: 0.5pu trec2: 450mS Urec2: 0.9pu trec3: 450mS PPMs Uret: 0pu tclear: 150mS Uclear: 0pu trec1: 150mS Urec1: 0pu trec2: 150mS Urec2: 0.9pu trec3: 3000mS | 1 - TSO internal consideration | [15 empty] | 0 - no consideration | Synchronous Generators Uret: 0.3pu tclear: 150ms Uclear: 0.7pu trec1: 150ms Urec1: 0.7pu trec2: 150ms Urec2: 0.9pu trec3: 1 s PPM Uret: 0.15pu tclear: 150ms Uclear: 0.15pu trec1: 150ms Urec1: 0.15pu trec2: 150ms Urec2: 0.9 pu trec3: 1,5 s U > 110 kV; Synchronous Generators Uret: 0pu tclear: 150ms Uclear: 0,25pu trec1: 325ms Urec1: 0.5pu trec2: 325ms Urec2: 0.9pu trec3: 1 s PPM Uret: 0pu tclear: 150ms Uclear: 0pu trec1: 150ms Urec1: 0 pu trec2: 150ms Urec2: 0.9 pu trec3: 1,5 s |  | sync. PGMs: Uret: 0 tclear: 0,15 Uclear: 0,25 trec1: 0,45 Urec1: 0,5 trec2: 0,7 Urec2: 0,85 trec3: 1,5 Tabela 7.2 Parametry dotyczące rys. 3 w zakresie zdolności modułów parku energii do pozostania w pracy podczas zwarcia Parametry napięcia [pu] Parametry czasu [s] Uret: 0 tclear: 0,15 Uclear: 0 trec1: 0,15 Urec1: 0 trec2: 0,15 Urec2: 0,85 trec3: 2,5 | 1 - TSO internal consideration |  |  |  | 3 - selected for approval |  |  |  |  | studies undergoing | 1 - TSO internal consideration | Synchronous Generators Uret: 0.0pu tclear: 250ms Uclear: 0.25pu trec1: 250ms Urec1: 0.5pu trec2: 250ms Urec2: 0.85pu trec3: 1,5s PPM Uret: 0.0pu tclear: 250ms Uclear: 0.0pu trec1: 250ms Urec1: 0.0pu trec2: 250ms Urec2: 0.85pu trec3: 1,5 s | 1 - TSO internal consideration
|  |  | 16.3.c | TSO |  |  |  | X | voltage-against-time profile for asymmetric faults | Further considerations mainly depend on outcomes of an ongoing R&D project | 1 - TSO internal consideration |  |  | The diagram for FRT capability to withstand asymetric faults will be identical with the one requested to be witstand for symetric one. | 2b – preliminary shared with stakeholders and publicly available | U ≥ 0 t ≤ 0.15s; U ≥ 0.25 t ≤ 0.7s; U ≥ 0.5 t ≤ 1.0s; U ≥ 0.7 t ≤ 1.5s | 2a - preliminary: shared with stakeholders, but not publicly available |  | 1 - TSO internal consideration |  |  |  |  | - sync. PGM: Uret: 0 Uclear: 0,25 Urec1: 0,6 Urec2: 0,75 tclear: 0,22 s trec1: 0,45 s trec2: 0,6 s trec3: 3 s - PPM: Uret: 0 Uclear: 0 Urec1: 0 Urec2: 0,75 tclear: 0,15 s trec1: 0,15 s trec2: 0,15 s trec3: 3 s | 2b - preliminary: shared with stakeholders and publicly available | Defined only available in PPT. |  |  |  |  | 2b - preliminary: shared with stakeholders and publicly available |  |  |  | 2 - preliminary shared with stakeholders |  |  |  |  | no difference between symetric and asymetric faults |  |  | Same as 16.3.a(i) | 1 - TSO internal consideration | [15 empty] | 0 - no consideration | Identical to symmetric | 0 - no consideration | the same profile as for symetric faults, see above | 1 - TSO internal consideration |  |  |  | 3 - selected for approval |  |  |  |  | studies undergoing | 1 - TSO internal consideration | As for symmetrical fault | 1 - TSO internal consideration
| ACTIVE POWER CONTROLLABILTY AND CONTROL RANGE |  | 15.2.a | RSO or TSO |  |  | X | X | time period to reach the adjusted active power set point | Inverter-connected generators shall reach the new setpoint within 1 minute Synchronous generators shall reach the new setpoint within 5 minutes | 1 - TSO internal consideration |  |  |  |  | In accordance with the requirements of the TSO and the technical capabilities | 2a - preliminary: shared with stakeholders, but not publicly available | defined in prequalification documents | 4 - approved/binding |  |  |  |  | to be defined project-specific |  | 10 sec | [13 empty] | PGM: The time period depends on the technology, generators set point at the time of instruction and defined minimum rates of active power change (2 % Pr/min for TPP and 1 % Pr/sec for HPP); PPM: time of response is 1 minute. |  |  | 10 seconds initiation and thereafter a ramp rate of 3% of rated maximum capacity | 1 - TSO internal consideration | [6 empty] | to be confirmed | [7 empty] | Value to be termined in connection aggreement for individual plants | 1 - TSO internal consideration | Hydro: 40%/min Gas: 10-20%/min Power park modules; 200%/min Others; 4%/min | 2a - preliminary: shared with stakeholders, but not publicly available | 15min | 1 - TSO internal consideration |  |  | The time period to reach the adjusted active power setpoint is corelate with the rate of change of active power of 2-10% Pn / min depending on the technology, the dead time (the time of the prime mover ) is 2 seconds, and the tolerance to achieve reference is 1% Pn | 3 - selected for approval |  |  |  |  | studies undergoing | 1 - TSO internal consideration | Project specific req. | 1 - TSO internal consideration
[9 empty] | tolerance applying to the new set point and the time to reach it. | tolerance level = +/- 5 % of nominal power | 1 - TSO internal consideration |  |  |  |  | In accordance with the requirements of the TSO and the technical capabilities | 2a - preliminary: shared with stakeholders, but not publicly available | defined in prequalification documents | 1 - TSO internal consideration |  |  |  |  | to be defined project-specific |  | to be defined | [13 empty] | between ±1% Pn and ±5% Pn (to be defined) |  |  | 1% | 1 - TSO internal consideration | [6 empty] | to be confirmed | [7 empty] | +/- 2% | 1 - TSO internal consideration | Whichever lower; +/- 2% of setpoint +/- 0,5% of nominal power | 1 - TSO internal consideration | 1% | 1 - TSO internal consideration |  |  |  | 3 - selected for approval |  |  |  |  | studies undergoing | 1 - TSO internal consideration | Project specific req. | 1 - TSO internal consideration
| AUTOMATIC DISCONNECTION DUE TO VOLTAGE LEVEL |  | 15.3 | RSO TSO |  |  | X | X | voltage criteria and technical parameters at the connection point for automatic disconnection |  | 1 - TSO internal consideration |  |  | There is no general need for automatic disconnection except for specific connection projects. The terms and settings for actual automatic disconnection of power-generating modules shall be specified by the relevant system operator in coordination with the relevant TSO. The grid user should communicate the settings of the protection scheme to be validated by the TSO. Automatic reconnection to the network after a disconnection event is not authorized and should be coordinated by the TSO in line with the Policy 5 (UCTE Operation Handbook) | 1 - TSO internal consideration | U>1.2 p.u. t=3s. U>1.3 p.u .t=1s.; | 2a - preliminary: shared with stakeholders, but not publicly available |  | 1 - TSO internal consideration |  |  |  |  | admissible disconnection at U > 1,1pu (400 kV) or U > 1,15pu (220 kV), or U < 0,85pu | 2b - preliminary: shared with stakeholders and publicly available | to be defined |  |  |  | only for radial distribution grids: U < 0,85 pu t=1,5 sec; 1,10 pu > U >= 1,15 pu t=0,8 sec; U>1,15pu t=0,2 sec | 2 - preliminary shared with stakeholders | not to violate FRT and continuous operational requirements by RSO | 1 - TSO internal consideration |  | 0 - no consideration |  |  |  |  | automatic disconnection for U<80% Un and U>120% Un |  |  | Disconnection relay shalle be capable of a setting between 0.9 and 1.118PU - site specific setting to be applied | 1 - TSO internal consideration | [16 empty] | Voltagerange; Disconnection if 1,1pu or 1,05pu for 60 min U < 0,9 pu FRT applies in addition to the above | 2a - preliminary: shared with stakeholders, but not publicly available | project specific | 1 - TSO internal consideration | [8 empty] | studies undergoing | 1 - TSO internal consideration | n/a for Type D; defined by DSOs. | 0 - no consideration
| VOLTAGE RANGES |  | 16.2.a.(i) | TSO |  |  |  | X | for Continental Europe time period for operation in the voltage range 1,118 pu-1,15 pu for PGM connected between 110kV and 300 kV | Considerations for 400 kV are crucial (1,05 - 1,10 p.u.) | 1 - TSO internal consideration |  |  | 20 minutes | 1 - TSO internal consideration | 20 min | 2a - preliminary: shared with stakeholders, but not publicly available |  | 1 - TSO internal consideration |  |  | 60 min | 2 - preliminary shared with stakeholders | 30 min | 2b - preliminary: shared with stakeholders and publicly available | to be defined |  |  |  | 60 mins | 2b - preliminary: shared with stakeholders and publicly available | 60 min | 1 - TSO internal consideration | 20 min | 2 - preliminary shared with stakeholders |  |  |  |  | 60 minutes |  |  | N/A | 0 - no consideration | [16 empty] | n/a |  | 1,118 pu – 1,15 pu 60 min 1,05 pu – 1,10 pu 60 min | 1 - TSO internal consideration |  |  | Voltage range---Time period for operation 0,85 pu – 0,90 pu---60 minutes 0,90 pu – 1,118 pu---unlimited 1,118 pu – 1,15 pu---60 minutes between 110kV and 220 kV | 3 - selected for approval |  |  |  |  | studies undergoing | 1 - TSO internal consideration | 20 min | 1 - TSO internal consideration
|  | X | 16.2.a.(ii) | TSO |  |  |  | X | determination of shorter time periods in the event of simultaneous overvoltage and under frequency or simultaneous under voltage and over frequency |  | 1 - TSO internal consideration |  |  | Project specific |  | n/a |  |  | 1 - TSO internal consideration |  |  |  |  | to be defined project-specific |  | to be defined |  |  |  | relaxation according to IEC | 2b - preliminary: shared with stakeholders and publicly available | no ease | 1 - TSO internal consideration | GRT proposal : 20 min Stakeholders don't agree | 2 - preliminary shared with stakeholders |  |  |  |  | 30 minutes if frequency is <48,5 Hz or >51 Hz |  |  | None | 1 - TSO internal consideration | [17 empty] | 0 - no consideration | n/a |  |  |  | no | 0 - no consideration |  |  |  |  | n/a |  | no | 1 - TSO internal consideration
|  | X | 16.2.a.(iii) | TSO |  |  |  | X | for Spain time period for operation in the voltage range 1,05 pu-1,0875 pu for PGMs connected between 300kV and 400 kV may be specified as unlimited |  | 0 - no consideration |  |  | N/A |  | n/a |  |  | 0 - no consideration |  |  |  |  | n/a |  | n/a |  |  |  | 1,0875 pu is being considered instead | 2b - preliminary: shared with stakeholders and publicly available |  |  | n/a | [8 empty] | N/A | 0 - no consideration | [16 empty] | n/a |  | n/a |  |  |  | n/a | 0 - no consideration |  |  |  |  | n/a
|  | X | 16.2.a.(v) | TSO |  |  |  | X | for Baltic voltage ranges and time period for operation may be specified in line with continental Europe for facilities connected for 400 kV |  | 0 - no consideration |  |  | N/A |  | n/a |  |  | 0 - no consideration |  |  |  |  | n/a |  | n/a |  |  |  | n/a |  |  |  | n/a | [8 empty] | N/A | 0 - no consideration | [16 empty] | n/a |  | n/a | [9 empty] | studies undergoing | 1 - TSO internal consideration
| REACTIVE POWER CAPABILITY FOR SYNCHRONOUS PGM | X | 17.2.a | RSO |  | X | X | X | capability to supply or absorb reactive power |  | 1 - TSO internal consideration |  |  | B SPGM = -25% PD/+48%PD with PD=0.9*Snom | 2b – preliminary shared with stakeholders and publicly available | n/a |  |  | 1 - TSO internal consideration |  |  |  |  | n/a to type D PGMs |  | n/a for type D PGM |  |  |  | P/Q diagram: Q/Pmax range: 0.6 | 2 - preliminary shared with stakeholders | RSO decides, 0,67 Q/Pmax maximum | 1 - TSO internal consideration | P/Q diagramm : - Q/Pmax range : 0,67 | 2 - preliminary shared with stakeholders |  |  |  |  | PGM and PPM type D: Q/Pmax range: at least 0,33 in both directions (lead, lag); TSO may consider different ratio for specific projects. Sync. generators have to operate within full range of their reactive capability curves; will be defined by DSO for generators type B and C; |  |  | Site specfic and to be specified by DSOs (N/A for TSO) | 1 - TSO internal consideration | [7 empty] | 1 - TSO internal consideration | [8 empty] | Case specific, but subject to national guidelines. 17.2.a is considered exhaustive | 2a - preliminary: shared with stakeholders, but not publicly available | Reference values of reactive power at P=Pmax: cos ϕ=0,85 for production reactive power j and cos ϕ=0,95 for consumption reactive power. If P<Pmax SyPGM shall generate reactive power according to P-Q-capability diagram. Binding values to be defined as project-specific by RSO. | 1 - TSO internal consideration | [8 empty] | studies undergoing | 1 - TSO internal consideration | n/a for Type D; defined by DSOs. | 0 - no consideration
| SUPPLEMENTARY REACTIVE POWER FOR SYNCHRONOUS PGM | X | 18.2.a | RSO |  |  | X | X | definition of supplementary reactive power to compensate for the reactive power demand of the high-voltage line or cable when the connection point is not located at the HV side of the step-up transformer |  | 1 - TSO internal consideration |  |  |  | 0 - no consideration | n/a |  |  | 1 - TSO internal consideration |  |  |  |  | to be defined project-specific |  | to be defined |  |  |  | n/a |  | Synchronous machine cos phi 0,95cap to 0,90 ind | 1 - TSO internal consideration | n/a | [5 empty] | site-specific. TSO may define supllementary reactive power capability for sync. PGM type D |  |  | Site-specific but generally right should be reatained | 1 - TSO internal consideration | [7 empty] | 1 - TSO internal consideration | [8 empty] | Case specific, but subject to national guidelines. 18.2.a is considered exhaustive | 2a - preliminary: shared with stakeholders, but not publicly available | to be defined project-specific | 1 - TSO internal consideration |  |  | with regard to reactive power capability, the relevant system operator may specify supplementary reactive power to be provided if the connection point of a synchronous power-generating module is neither located at the highvoltage terminals of the step-up transformer to the voltage level of the connection point nor at the alternator terminals, if no step-up transformer exists. This supplementary reactive power shall compensate the reactive power demand of the high-voltage line or cable between the highvoltage terminals of the step-up transformer of the synchronous power-generating module or its alternator terminals, if no step-up transformer exists, and the connection point and shall be provided by the responsible owner of that line or cable | 3 - selected for approval |  |  |  |  | studies undergoing | 1 - TSO internal consideration |  | 0 - no consideration
| REACTIVE POWER CAPABILITY AT MAXIMUM CAPACITY FOR SYNCHRONOUS PGM |  | 18.2.b.(i) | RSO TSO |  |  | X | X | definition of a U-Q/Pmax-profile at maximum capacity | Definitions of the requirement are partly implemented in national policies, but they are not fully compliant according to the NC | 1 - TSO internal consideration |  |  | Under discussion | 1 - TSO internal consideration | DQ/Pmax=0,53p.u.; DU=0,15 p.u. | 2a - preliminary: shared with stakeholders, but not publicly available |  | 1 - TSO internal consideration |  |  |  |  | under discussion |  | to be defined |  |  |  | U/Q diagramm : -voltage range : 0,2 pu - Q/Pmax range : 0,6 | 2b - preliminary: shared with stakeholders and publicly available | voltage 0,15 pu 0,67 Q/Pmax | 1 - TSO internal consideration | U/Q diagramm : -voltage range : 0,2 pu - Q/Pmax range : 0,67 | 2 - preliminary shared with stakeholders |  |  |  |  | -voltage range : 0,225 pu - Q/Pmax range : 0,66 |  |  | -0.45 (lead) to +0.55 (lag) Q/Pmax for normal voltage range of 0.9pu - 1.118 pu (unlimited) | 1 - TSO internal consideration | [6 empty] | tbc | [9 empty] | Case specific, but subject to national guidelines. 18.2.b is considered exhaustive | 2a - preliminary: shared with stakeholders, but not publicly available | In attachment "PL_Art. 18.2.b.(i)_Confidential.png" | 1 - TSO internal consideration |  |  | Maximum range of Q/Pmax---0,95 Maximum range of voltage levels in steady state defined in relative units pu---0,225 | 3 - selected for approval |  |  |  |  | studies undergoing | 1 - TSO internal consideration | Maximum range of Q/Pmax---0,95 Maximum range of voltage levels in steady state defined in relative units pu---0,225 | 1 - TSO internal consideration
| VOLTAGE STABILITY FOR SYNCHRONOUS PGM |  | 19.2.b.(v) | TSO |  |  |  | X | power threshold above which a PSS function is to be specified | Currently there are is no obligation for PGFOs to install PSS | 1 - TSO internal consideration |  |  | from >25MW but site specific activation and tuning of the parameters | 2b – preliminary shared with stakeholders and publicly available | All sync. PGM | 2a - preliminary: shared with stakeholders, but not publicly available |  | 1 - TSO internal consideration |  |  |  |  | all type D sync. PGM | 2b - preliminary: shared with stakeholders and publicly available | P>20% of Pn |  |  |  | above 50 MW (type D) SPGM | 2b - preliminary: shared with stakeholders and publicly available | type D | 1 - TSO internal consideration | type D SPGM | 2 - preliminary shared with stakeholders |  |  |  |  | TSO may require PSS function for sync. PGM type D under certain conditions (3 phase short-circuit power at the connection node should be larger than 4xPmax) |  |  | 10MW | 1 - TSO internal consideration | [6 empty] | tbc | 1 - TSO internal consideration | [8 empty] | Type D - 30 MW |  | 20 MW | 1 - TSO internal consideration |  |  | Usually, this limit is 150 MW | 3 - selected for approval |  |  |  |  | studies undergoing | 1 - TSO internal consideration | 50 MVA | 1 - TSO internal consideration
| REACTIVE POWER CAPABILITY FOR PPM | X | 20.2.a | RSO |  | X | X | X | capability to supply or absorb reactive power |  | 1 - TSO internal consideration |  |  | Triangular form, -30%PD/+33%PD with PD=0.95*SNOM Page 10 | 2b – preliminary shared with stakeholders and publicly available | n/a |  |  | 1 - TSO internal consideration |  |  |  |  | n/a to type D PGMs |  | n/a for type D PGM |  |  |  | P/Q diagram: Q/Pmax range: 0.6 | 2b - preliminary: shared with stakeholders and publicly available | RSO decides, 0,67 Q/Pmax maximum | 1 - TSO internal consideration | P/Q diagramm: - Q/Pmax range : 0,67 | 2 - preliminary shared with stakeholders |  |  |  |  | Q/Pmax range: 0.33 in both direction (at the connection point) |  |  | DSOs to specify but expected they will request to match 21.3.B | 1 - TSO internal consideration | [7 empty] | 1 - TSO internal consideration | [8 empty] | Case specific, but subject to national guidelines. 20.2.a is considered exhaustive | 2a - preliminary: shared with stakeholders, but not publicly available | Reference values of reactive power at P=Pmax: cos ϕ=0,95 in both direction: production and consumption reactive power. If P<Pmax PPM shall generate reactive power according to P-Q-capability diagram. Binding values to be defined as project-specific by RSO | 1 - TSO internal consideration |  |  | yes | 1 - TSO internal consideration |  |  |  |  | studies undergoing | 1 - TSO internal consideration | n/a for Type D; defined by DSOs. | 0 - no consideration
| FAST FAULT CURRENT INJECTION FOR PPM | X | 20.2.b | RSO TSO |  | X | X | X | Specifications of: - how and when a voltage deviation is to be determined as well as the end of the voltage deviation - fast fault current characteristics - timing and accuracy of the fast fault current, which may include several stages during a fault and after its clearance |  | 1 - TSO internal consideration |  |  | Site specific activation and tuning of the parameters 20170201_SGU_Technical_Summary_TFINCs.pdf Page 12 | 2b – preliminary shared with stakeholders and publicly available | n/a |  |  | 1 - TSO internal consideration |  |  |  |  | - fault identification: phase-to-phase U < 90% or >110% - end of fault: 90% < U < 110% - fault current: Di = k*Du; 2 ≤ k ≤ 6 - fault current rise time: ≤ 30 ms fault current settlement time: ≤ 60 ms | 2b - preliminary: shared with stakeholders and publicly available | under consideration |  |  |  | close to german public available proposal with some modifications; still under discussion with SH | 2a - preliminary: shared with stakeholders, but not publicly available | TBD | 1 - TSO internal consideration | under discussion | [5 empty] | no requests |  |  | Active power output is maintained proportional to voltage dip for at least 500mS | 1 - TSO internal consideration | [7 empty] | 1 - TSO internal consideration | [8 empty] | Voltage threshold; 0,85 pu Characteristics; adjustable prioritizing between active and reactiv by K factor or by specifying voltagelevel with full contribution Should be activated within 60 ms and fully regulated within 1 second | 1 - TSO internal consideration | Under discussion | 1 - TSO internal consideration |  |  |  | 3 - selected for approval |  |  |  |  | studies undergoing | 1 - TSO internal consideration | Non mandatory/specify in the contract | 1 - TSO internal consideration
|  | X | 20.2.c | RSO TSO |  | X | X | X | specifications for asymmetrical current injection, in case of asymmetric faults (1-phase or 2-phase) |  | 1 - TSO internal consideration |  |  | The diagram for FRT capability to withstand asymetric faults will be identical with the one requested to be witstand for symetric one. | 2b – preliminary shared with stakeholders and publicly available | n/a |  |  | 1 - TSO internal consideration |  |  |  |  | fault current specification applies to positive and negative sequence current | 2b - preliminary: shared with stakeholders and publicly available | under consideration |  |  |  | close to german public available proposal with some modifications; still under discussion with SH | 2a - preliminary: shared with stakeholders, but not publicly available | TBD |  | under discussion | [5 empty] | no requests |  |  | Active power output is maintained proportional to voltage dip for at least 500mS | 1 - TSO internal consideration | [7 empty] | 1 - TSO internal consideration | [9 empty] | 0 - no consideration | Under discussion | 1 - TSO internal consideration |  |  |  | 3 - selected for approval |  |  |  |  | studies undergoing | 1 - TSO internal consideration | Non mandatory/specify in the contract | 1 - TSO internal consideration
| SUPPLEMENTARY REACTIVE POWER FOR PPM | X | 21.3.a | RSO |  |  | X | X | definition of supplementary reactive power for a PPM whose connection point is not located at the high-voltage terminals of its step-up transformer nor at the terminals of the high-voltage line or cable to the connection point at the PPM, if no step-up transformer exists |  | 1 - TSO internal consideration |  |  |  |  | n/a |  |  | 1 - TSO internal consideration |  |  |  |  | to be defined project-specific |  | to be defined |  |  |  | n/a |  | TBD |  | N/A | [5 empty] | site-specific. TSO may define supllementary reactive power capability for PPM type D |  |  | Site-specific but generally right should be reatained | 1 - TSO internal consideration | [7 empty] | 1 - TSO internal consideration | [8 empty] | Case specific, but subject to national guidelines. 21.3.a is considered exhaustive | 2a - preliminary: shared with stakeholders, but not publicly available | project specific | 1 - TSO internal consideration |  |  |  | 0 - no consideration |  |  |  |  | studies undergoing | 1 - TSO internal consideration |  | 0 - no consideration
| REACTIVE POWER CAPABILITY AT MAXIMUM CAPACITY FOR PPM |  | 21.3.b | RSO TSO |  |  | X | X | definition of a U-Q/Pmax-profile at maximum capacity |  | 1 - TSO internal consideration |  |  | Range: -25%Pmax/+45%Pmax with a voltage dependency (for high voltages lower erequirement for high qinj and for low voltages lower requirement for Qabs). http://www.elia.be/~/media/files/Elia/users-group/2016_TF%20Implementation%20NCs/20170201_SGU2_Session1/20170201_SGU_Technical_Summary_TFINCs.pdf Page 18 | 2b - preliminary: shared with stakeholders and publicly available | DQ/Pmax=0,62 p.u.; DU=0,220 p.u. | 2a - preliminary: shared with stakeholders, but not publicly available |  | 1 - TSO internal consideration |  |  |  |  | under discussion |  | to be defined |  |  |  | U/Q diagramm : -voltage range : 0,2 pu - Q/Pmax range : 0,6 | 2b - preliminary: shared with stakeholders and publicly available | voltage 0,15 pu 0,67 Q/Pmax | 1 - TSO internal consideration | U/Q diagramm : -voltage range : 0,2 pu - Q/Pmax range : 0,67 | 2 - preliminary shared with stakeholders |  |  |  |  | -voltage range : 0,225 pu - Q/Pmax range : 0,66 |  |  | +/- 0.33 Q/Pmax for 1.118PU to 0.9PU nominal voltage | 1 - TSO internal consideration | [7 empty] | 1 - TSO internal consideration | [8 empty] | Case specific, but subject to national guidelines. 21.3.b is considered exhaustive | 2a - preliminary: shared with stakeholders, but not publicly available | In attachment "PL_Art. 21.3.b_Confidential.png" | 1 - TSO internal consideration |  |  | Q/Pmax=0,75 ; V=0,200 u.r | 1 - TSO internal consideration |  |  |  |  | studies undergoing | 1 - TSO internal consideration
| REACTIVE POWER CAPABILITY BELOW MAXIMUM CAPACITY FOR PPM |  | 21.3.c.(i) | RSO TSO |  |  | X | X | definition of a P-Q/Pmax-profile below maximum capacity |  | 1 - TSO internal consideration |  |  | under disscussion | 1 - TSO internal consideration |  | 2a - preliminary: shared with stakeholders, but not publicly available |  | 1 - TSO internal consideration |  |  |  |  | under discussion |  | to be defined |  |  |  | P from 100% to 20%--> Q= +/- 0.3 pu; P from 0% to 10% -->Q=5%; | 2b - preliminary: shared with stakeholders and publicly available | same as max capacity at P production above 10 % of Pmax | 1 - TSO internal consideration | P/Q diagramm : - Q/Pmax range : 0,67 | 2 - preliminary shared with stakeholders |  |  |  |  | U-Q/Pmax characteristic for P between Pmin and 100 % Pmax (Pmin is site-specific); for WPP: between P for cut-in speed and cut-out speed) |  |  | P/PU for 100% to 12% should be +/- 0.33 Q/Pmax for 1.118PU to 0.9PU nominal voltage P/PU below 12% - cut in speed be at maximum +/- Q/Pmax capability at start of MW power output (i.e. cut-in speed) | 1 - TSO internal consideration | [7 empty] | 1 - TSO internal consideration | [8 empty] | Case specific, but subject to national guidelines. 21.3.c is considered exhaustive | 2a - preliminary: shared with stakeholders, but not publicly available | In attachment "PL Art. 21.3.c.(i)_Confidential.png" | 1 - TSO internal consideration |  |  |  | 1 - TSO internal consideration |  |  |  |  | studies undergoing | 1 - TSO internal consideration |  | 1 - TSO internal consideration
|  |  | 21.3.c.(ii) | [12 empty] | DQ/Pmax=-0,28...+0,34=0,62p.u.; DP=1 p.u. | [9 empty] | to be defined | [16 empty] | Covered by 21.3.c.(i) requirements | 1 - TSO internal consideration | [28 empty] | studies undergoing |  | Max range of Q/Pmax 0,75
| VOLTAGE RANGES FOR OFFSHORE PPM |  | 25.1 | TSO |  |  |  |  | for Continental Europe time period for operation in the voltage range 1,118 pu-1,15 pu for PGM connected between 110kV and 300 kV |  | 0 - no consideration |  |  | 20 minutes | 2b – preliminary shared with stakeholders and publicly available | 20 min | 2a - preliminary: shared with stakeholders, but not publicly available |  | 1 - TSO internal consideration |  |  |  |  | 30 min | 2b - preliminary: shared with stakeholders and publicly available | to be defined |  |  |  | 60 mins | 2b - preliminary: shared with stakeholders and publicly available |  |  | 20 min | 2 - preliminary shared with stakeholders |  |  |  |  | up to 60 minutes |  |  | N/A | 0 - no consideration | [7 empty] | 0 - no consideration | [8 empty] | n/a |  | 60 min | 1 - TSO internal consideration |  |  | Voltage range---Time period for operation 0,85 pu – 0,90 pu---60 minutes 0,90 pu – 1,118 pu---unlimited 1,118 pu – 1,15 pu---60 minutes between 110kV and 220 kV | 1 - TSO internal consideration |  |  |  |  | studies undergoing | 1 - TSO internal consideration | n/a | 0 - no consideration
[9 empty] | - Parameters and settings of the components of the voltage control system |  | 0 - no consideration |  |  | Project specific | 2b – preliminary shared with stakeholders and publicly available | to be defined |  |  | 1 - TSO internal consideration |  |  |  |  | to be defined project-specific |  | to be defined |  |  |  | same as onshore | 2b - preliminary: shared with stakeholders and publicly available |  |  | to be defined project-specific | [5 empty] | no requests |  |  | Not sure why this is in the spreadsheet? | 0 - no consideration | [7 empty] | 0 - no consideration | [8 empty] | Subject to same agreements as in 19.2 | 2a - preliminary: shared with stakeholders, but not publicly available | n/a |  |  |  |  | 1 - TSO internal consideration |  |  |  |  | studies undergoing | 1 - TSO internal consideration | n/a | 0 - no consideration
[9 empty] | - Specifications of the AVR |  | 0 - no consideration |  |  | Project specifc | 2b – preliminary shared with stakeholders and publicly available | to be defined |  |  | 1 - TSO internal consideration |  |  |  |  | to be defined project-specific |  | to be defined |  |  |  | same as onshore | 2b - preliminary: shared with stakeholders and publicly available |  |  | to be defined project-specific | [5 empty] | no requests |  |  | Use BS4999 part 140, Category 1 | 1 - TSO internal consideration | [7 empty] | 0 - no consideration | [8 empty] | Subject to same agreements as in 19.2 | 2a - preliminary: shared with stakeholders, but not publicly available | n/a |  |  |  |  | 1 - TSO internal consideration |  |  |  |  | studies undergoing | 1 - TSO internal consideration | n/a | 0 - no consideration
| VOLTAGE RANGES |  | 25.1 | TSO |  |  |  |  | For Continental Europe time period for operation in the voltage range 1,118 pu-1,15 pu, 1,05pu-1,10pu for PGM |  | 1 - TSO internal consideration |  |  | 20 minutes | 2b – preliminary shared with stakeholders and publicly available | 20 min | 2a - preliminary: shared with stakeholders, but not publicly available |  | 1 - TSO internal consideration |  |  |  |  | 30 min | 2b - preliminary: shared with stakeholders and publicly available | to be defined |  |  |  | same as onshore | 2b - preliminary: shared with stakeholders and publicly available |  |  | 20 min | 2 - preliminary shared with stakeholders |  |  |  |  | up to 60 minutes |  |  | N/A | 0 - no consideration | [7 empty] | 0 - no consideration | [8 empty] | n/a |  | 60 min | 1 - TSO internal consideration |  |  |  | 1 - TSO internal consideration |  |  |  |  | studies undergoing | 1 - TSO internal consideration | n/a
[9 empty] | For Nordic time period for operation in the voltage range 1,05pu-1,10pu for PGM |  | 0 - no consideration |  |  | N/A |  | n/a |  |  | 0 - no consideration |  |  |  |  | n/a |  | to be defined |  |  |  | n/a |  |  |  | n/a | [5 empty] | no requests |  |  | N/A | 0 - no consideration | [7 empty] | 0 - no consideration | [8 empty] | 60 min | 2a - preliminary: shared with stakeholders, but not publicly available | n/a |  |  |  | n/a | 1 - TSO internal consideration |  |  |  |  | n/a
|  | X | 16.2.a.(iii) | TSO |  |  |  |  | For Spain time period for operation in the voltage range 1,05 pu-1,0875 pu for PGMs connected between 300kV and 400 kV may be specified as unlimited |  | 0 - no consideration |  |  | N/A |  | n/a |  |  | 0 - no consideration |  |  |  |  | n/a |  | n/a |  |  |  | same as onshore | 2b - preliminary: shared with stakeholders and publicly available |  |  | n/a | [5 empty] | no requests |  |  | N/A | 0 - no consideration | [7 empty] | 0 - no consideration | [8 empty] | n/a |  | n/a |  |  |  | n/a | 1 - TSO internal consideration |  |  |  |  | n/a
|  | X | 16.2.a.(v) | TSO |  |  |  |  | For Baltic voltage ranges and time period for operation may be specified in line with continental Europe for facilities connected for 400 kV |  | 0 - no consideration |  |  | N/A |  | n/a |  |  | 0 - no consideration |  |  |  |  | n/a |  | n/a |  |  |  | n/a |  |  |  | n/a | [5 empty] | no requests |  |  | N/A | 0 - no consideration | [7 empty] | 0 - no consideration | [8 empty] | n/a |  | n/a |  |  |  | n/a | 1 - TSO internal consideration |  |  |  |  | n/a
| REACTIVE POWER CAPABILITY AT MAXIMUM CAPACITY FOR OFFSHORE PPM |  | 25.5 | TSO |  |  |  |  | Definition of the U-Q/Pmax-profile at Pmax | Offshore not relevant for AT | 0 - no consideration |  |  | Same as type D PPM | 2b – preliminary shared with stakeholders and publicly available | Under discussion |  |  | 0 - no consideration |  |  |  |  | under discussion |  | to be defined |  |  |  | same as onshore | 2b - preliminary: shared with stakeholders and publicly available |  |  | U/Q diagramm : -voltage range : 0,2 pu - Q/Pmax range : 0,67 | 2 - preliminary shared with stakeholders |  |  |  |  | -voltage range : 0,225 pu - Q/Pmax range : 0,66 (default); up to 0,75 (site-specific) |  |  | +/- 0.33 Q/Pmax for 1.118PU to 0.9PU nominal voltage | 1 - TSO internal consideration | [7 empty] | 0 - no consideration | [8 empty] | Case specific, but subject to national guidelines. 25.5 is considered exhaustive | 2a - preliminary: shared with stakeholders, but not publicly available | In attachment "PL_Art. 25.05__Confidential.png" | 1 - TSO internal consideration |  |  |  | 1 - TSO internal consideration |  |  |  |  | studies undergoing | 1 - TSO internal consideration | n/a | 0 - no consideration
SYSTEM RESTORATION | CAPABILITY OF RECONNECTION AFTER AN INCIDENTAL DISCONNECTION CAUSED BY A NETWORK DISTURBANCE |  | 14.4.a | TSO |  | X | X | X | conditions for reconnection to the network after an incidental disconnection caused by network disturbance |  | 1 - TSO internal consideration |  |  |  |  | Under discussion |  |  | 1 - TSO internal consideration |  |  |  |  | 47,5 Hz ≤ f ≤ 51,5Hz 198 kV ≤ U ≤ 250 kV 360 kV ≤ U ≤ 430 kV | 2b - preliminary: shared with stakeholders and publicly available | to be defined |  |  |  | frequency and voltage inside ranges | 2b - preliminary: shared with stakeholders and publicly available | [8 empty] | Defined accroding to the connection agreement. TSO approval for each type D PGM and PPM reconnection necessary. GENERAL CONDITIONS: 47,5 Hz ≤ f ≤ 51,5Hz 0,85 pu ≤ U ≤ 1,15 pu |  |  | Site-specific for types B and C, Prohibited for D | 1 - TSO internal consideration | [6 empty] | tbc | 1 - TSO internal consideration | [8 empty] | Case specific, but subject to national guidelines. 14.4.a is considered exhaustive | 2a - preliminary: shared with stakeholders, but not publicly available | 49,5 Hz ≤ f ≤ 50,05 Hz 0,85 ≤ U ≤ 1,118 | 1 - TSO internal consideration |  |  | a power-generating module is capable of reconnecting to the network after an incidental disconnection caused by a network disturbance automatical or at dispach dispozal (C and D) | 3 - selected for approval |  |  |  |  | studies undergoing | 1 - TSO internal consideration | tbc | 1 - TSO internal consideration
|  |  | 14.4.b | TSO |  | X | X | X | conditions for automatic reconnection |  | 1 - TSO internal consideration |  |  | Automatic reconnection not allowed | 2b – preliminary shared with stakeholders and publicly available | Under discussion |  |  | 1 - TSO internal consideration |  |  |  |  | 48,5 Hz ≤ f ≤ 50,1 Hz 210 kV ≤ U 370 kV ≤ U | 2b - preliminary: shared with stakeholders and publicly available | to be defined |  |  |  | frequency and voltage inside ranges | 2b - preliminary: shared with stakeholders and publicly available | [8 empty] | Defined accroding to the connection agreement. SPECIFIC CONDITIONS: Δf≤200 mHz; ΔU≤20 kV; Δδ≤30⁰ |  |  | Site-specific | 1 - TSO internal consideration | [6 empty] | tbc | 1 - TSO internal consideration | [8 empty] | Case specific, but subject to national guidelines. 14.4.a is considered exhaustive | 2a - preliminary: shared with stakeholders, but not publicly available | 49,5 Hz ≤ f ≤ 50,05 Hz 0,85 ≤ U ≤ 1,118 | 1 - TSO internal consideration |  |  | in frequency range 47,5-51,5 Hz and voltage 0.85 - 1,1 Un | 3 - selected for approval |  |  |  |  | studies undergoing | 1 - TSO internal consideration | tbc | 1 - TSO internal consideration
| OPERATION FOLLOWING TRIPPING TO HOUSELOAD |  | 15.5.c.(iii) | RSO TSO |  |  | X | X | minimum operation time within which the PGM is capable of operating after tripping to house load |  | 1 - TSO internal consideration |  |  |  |  | 2 h | 2a - preliminary: shared with stakeholders, but not publicly available |  | 1 - TSO internal consideration |  |  |  |  | 2 h | 2b - preliminary: shared with stakeholders and publicly available | applying for derogation |  |  |  | 4 h | 2b - preliminary: shared with stakeholders and publicly available | [8 empty] | no general specification. Depending on the PGM type and defined within connection agreement. General value 2 hours. |  |  | 4 hours | 1 - TSO internal consideration | [7 empty] | 1 - TSO internal consideration | [8 empty] | 2 hours | 1 - TSO internal consideration | min. 12 h - technical capability; compliance time 2 h | 1 - TSO internal consideration |  |  | the PGM synchronous should be able to operate after triping to house load at least 1 hours in order to participate in the restoration SEN | 3 - selected for approval |  |  |  |  | studies undergoing | 1 - TSO internal consideration | 2 h | 1 - TSO internal consideration
| ACTIVE POWER RECOVERY FOR SYNCHRONOUS PGM |  | 17.3 | TSO |  | X | X | X | definition of the magnitude and time for active power recovery |  | 1 - TSO internal consideration |  |  |  |  | 1,5 s | 2a - preliminary: shared with stakeholders, but not publicly available |  | 1 - TSO internal consideration |  |  |  |  | as fast as possible and < 6s if U ≤ 20%; < 3s if U > 20% | 2b - preliminary: shared with stakeholders and publicly available | to be defined |  |  |  | depending on residual voltage of the fault: if U residual higher than 0,2 pu--> SPGM must recover 95% of previous P in a time lower than 1 sec once voltage has recovered up to 0,85 pu and the rest pf P within next 2 sec; if U residual lower than 0,2 pu, SPGM shall recover 95% of its previous P in a time lower than 3 sec once U>0,85 and the rest of P within next 2 sec | 2b - preliminary: shared with stakeholders and publicly available | [8 empty] | active power recovery at value before incident as soon as possible. Special requests according to the stability studies. |  |  | 90% of available power as quickly as technology allows but within 500mS after voltage has recovered to 90% of nominal voltage for faults within 140mS. For longer time periods 90% within 1 sec on recovery to 90% of nomnal voltage | 1 - TSO internal consideration | [7 empty] | 1 - TSO internal consideration | [8 empty] | Active power recovery is considered to be a inherent capability and maintained through FRT-requirements. | 1 - TSO internal consideration | as fast as possible, considering inherent feature of synchronous PGMs | 1 - TSO internal consideration |  |  | active power recovery at value before incident as soon as possible | 3 - selected for approval |  |  |  |  | studies undergoing | 1 - TSO internal consideration | tbc | 1 - TSO internal consideration
| POST FAULT ACTIVE POWER RECOVERY FOR PPM |  | 20.3.a | TSO |  | X | X | X | specifications of the post-fault active power recovery |  | 1 - TSO internal consideration |  |  | Site specific | 2b – preliminary shared with stakeholders and publicly available |  |  |  | 1 - TSO internal consideration | [10 empty] | coordinated with 20.3 and 20.2 | 2b - preliminary: shared with stakeholders and publicly available |  |  | under discussion | [5 empty] | Site specific; GENERAL REQUIREMENTS: active power recovery begins after 0,15 seconds; maximum recovery time is 5 seconds; active power magnitute is equal to pre-fault value; tolerance 10% | [11 empty] | 1 - TSO internal consideration | [14 empty] | active power equal with the minimum 80% from initial active power | 3 - selected for approval |  |  |  |  | studies undergoing | 1 - TSO internal consideration | tbc | 1 - TSO internal consideration
[9 empty] | Following specifications: - when the post-fault active power recovery begins, based on a voltage criteria - a maximum allowed time for active power recovery - a magnitude and accuracy for active power recovery |  | 1 - TSO internal consideration |  |  |  |  | Recovery starts after 0.15 sec. the maximum time is 1.5 sec. the size is reaching the previous active power with an accuracy of 10% | 2a - preliminary: shared with stakeholders, but not publicly available |  | 1 - TSO internal consideration |  |  |  |  | as fast as possible and < 1s | 2b - preliminary: shared with stakeholders and publicly available | to be defined |  |  |  | coordinated with 20.3 and 20.2 | 2b - preliminary: shared with stakeholders and publicly available |  |  | under discussion | [8 empty] | 90% of available power as quickly as technology allows but within 500mS after voltage has recovered to 90% of nominal voltage for fualts within 140mS. For longer time periods 90% within 1 sec on recovery to 90% of nomnal voltage | 1 - TSO internal consideration | [7 empty] | 1 - TSO internal consideration | [8 empty] | Voltage threshold; 0,90 pu recovery time; 1 second magnitude; 90% | 1 - TSO internal consideration | 90% U; 5 sec. | 1 - TSO internal consideration |  |  | ramprate of 10% Pn/sec, 5%Pn accurancy | 3 - selected for approval |  |  |  |  | studies undergoing | 1 - TSO internal consideration | tbc | 1 - TSO internal consideration
OTHER ASPECTS | INFORMATION EXCHANGES |  | 14.5.d | RSO or TSO |  | X | X | X | content of information exchanges and precise list and time of data to be facilitated. |  | 1 - TSO internal consideration |  |  |  |  | will be defined | [7 empty] | to be defined project-specific |  | to be defined.Stakeholder workshop in November 2017 |  |  |  | Defined in PO 9 (already in force) | 2b - preliminary: shared with stakeholders and publicly available |  |  | to be discussed in coordination with SOGL implementation | [5 empty] | For type D: minimum set of data: status of circuit breakers, disconnecting switches and tap-changer; measured values of voltage, frequency, active and reactive power; Other information are defined within the connection agreement. Measurement equipment specification, data acquisition and other aspects are defined within TSO document "Technical rules for the points of common couplings". |  |  | For type C and D Sync machines: the full list below applies, type B is a subset, yet to be defined. (a) LV switchgear positions pertinent to the status of each Grid Connected Transformer through a set of two potential free auxiliary contacts (one contact normally open and one contact normally closed when circuit breaker is open) for each circuit breaker; (b) kV at transformer low Voltage terminals; and (c) a minimum of four sets of normally open potential free auxiliary contacts in each transformer LV bay for fault indication. (d) MW and +/-Mvar at alternator terminals of each Generation Unit; (e) kV at Generator Transformer LV terminals; (f) Generator Transformer tap position; (g) Measured or derived MW output on each fuel, from Generation Units that can continuously fire on more than one fuel simultaneously; (h) Where it is agreed between the TSO and the Generator that signals are not available on the HV terminals, +/- MW and +/- Mvar shall be provided at the Grid Connected Transformer low Voltage terminals; and (i) Remaining Secondary Fuel capability (where applicable) in MWh equivalent when running at Registered Capacity; For type C and D PPMs: the full list below applies, type B is a subset, yet to be defined. a) Active Power output (MW) at the lower voltage side of the Grid Connected Transformer; b) Reactive Power output/demand (+/-Mvar) at the lower voltage side of the Grid Connected Transformer; c) Voltage (in kV) at the lower voltage side of the Grid Connected Transformer; d) Available Active Power (MW) at the lower voltage side of the Grid Connected Transformer; e) Grid Connected Transformer tap positions; f) Voltage Regulation Set-point (in kV); g) On/off status indications for all Reactive Power devices exceeding 5 Mvar; h) Circuit-breaker and disconnect position indication shall be required. These may include indications from MV circuit-breakers on individual WTG circuits. Signals from individual WTG circuit-breakers shall not be required. The actual circuit-breaker and disconnect signals required shall be specified by the TSO at least 120 Business Days prior to the Controllable WFPS’s scheduled Operational Date; i) A minimum of four sets of normally open potential free auxiliary contacts in each Grid Connected Transformer lower voltage bay for fault indications; and j) On/off status of TSO remote control enable switch, which disables the ability of the TSO to send commands to the Controllable WFPS. For the Controllable WFPS’s where the Connection Point is at the HV side of the Grid Connected Transformer, signals a), b) and c) above will also be required from the HV side of the Grid Connected Transformer. k) Controllable WFPS Active Power Control Set-point value (MW); l) Controllable WFPS Active Power Control status indication (ON/OFF). m) Frequency Response System mode signal (i.e. Power-Frequency Response Curve 1 or 2); n) Frequency Response System status indication (ON/OFF). o) Frequency Response System Governor Droop value. Standards for signals will be made publically available. | 1 - TSO internal consideration | [7 empty] | 1 - TSO internal consideration | [8 empty] | Case specific, but subject to national guidelines. 14.5.d is considered exhaustive | 2a - preliminary: shared with stakeholders, but not publicly available | project specific | 1 - TSO internal consideration |  |  | list of signals: -status signal of FSM (on/off), -scheduled active power output, - actual value of the active power output, -active power, reactive power, voltage as measured values and setpoints in the connection point - position of switch breaker and breaker at the point of connection / separation. | 3 - selected for approval |  |  |  |  | studies undergoing | 1 - TSO internal consideration | tbc
| LOSS OF ANGULAR STABILITY OR LOSS OF CONTROL |  | 15.6.a | RSO PGFO TSO |  |  | X | X | criteria to detect loss of angular stability or loss of control |  | 1 - TSO internal consideration |  |  |  |  | will be defined |  |  | 1 - TSO internal consideration |  |  |  |  | to be defined project-specific |  | to be defined.reusage of current requirement |  |  |  | n/a | [9 empty] | Project specific. Generator protection must include pole-slipping protection. Connection agreement has to include protection settings, based on specific analysis. |  |  | Site - specific | 1 - TSO internal consideration | [7 empty] | 1 - TSO internal consideration | [9 empty] | 0 - no consideration | under discussion | 1 - TSO internal consideration |  |  | There are no specific criteria to detect the loss of angular stability. However, offline analysis based on voltage, active power, reactive power and frequency records are asked for to detect loss of angular stability | 3 - selected for approval |  |  |  |  | studies undergoing | 1 - TSO internal consideration
| INSTRUMENTATION | X | 15.6.b.(i) | RSO |  |  | X | X | definition of the quality of supply parameters |  | 0 - no consideration |  |  |  |  | n/a |  |  | 1 - TSO internal consideration |  |  |  |  | under discussion |  | to be defined |  |  |  | flicker, harmonics, and unbalance requirements | 2b - preliminary: shared with stakeholders and publicly available |  |  | under discussion | [5 empty] | QUALITY OF SUPPLY PARAMETERS: harmonics (according to IEC/TR 61000-3-6); flickers (according to IEC/TR 61000-3-7); voltage unbalance (according to IEC/TR 61000-3-13); MEASUREMENT: each point of common cupling has to be equipped with voltage quality measurement device and fault recorder. ACCURACY: according to TSO and DSO technical standards |  |  | 61000-3-6 harmonic planning limit levels up to 20th Harmonic | 1 - TSO internal consideration | [7 empty] | 0 - no consideration | [9 empty] | 0 - no consideration | Accuracy: • voltage – 0,1%, • active power – 0,1%, • reactive power – 0,1%, • frequence – 0,01%. | 1 - TSO internal consideration |  |  | power-generating facilities shall be equipped with a facility to provide fault recording and monitoring of dynamic system behaviour. This facility shall record the following parameters: the voltages on all three phases, current on each phase, the three phase active and reactive power and the frequency | 3 - selected for approval |  |  |  |  | studies undergoing | 1 - TSO internal consideration | tbc
|  |  | 15.6.b.(ii) | RSO PGFO TSO |  |  | X | X | settings of the fault recording equipment, including triggering criteria and the sampling rates |  | 1 - TSO internal consideration |  |  |  |  | Depending on the specific case |  |  | 1 - TSO internal consideration |  |  |  |  | to be defined project-specific |  | to be defined |  |  |  | n/a | [9 empty] | According to TSO and DSO technical standards related to the points of common couplings |  |  | Site - specific | 1 - TSO internal consideration | [7 empty] | 1 - TSO internal consideration | [8 empty] | Case specific, but subject to national guidelines. 14.6.b.(ii) is considered exhaustive | 2a - preliminary: shared with stakeholders, but not publicly available | • for voltage ( average of 10-min measure from Urms ): a) voltage level 400 kV and above: URMS<0,9 pu or URMS>1,05 pu, b) voltage level 220 kV and 110 kV: URMS<0,9 pu or URMS>1,118 pu, c)voltage level 110 kV or below: URMS<0,9 pu or URMS>1,1 pu. • for frequence: f< 49,8 Hz or f>50,2 Hz. | 1 - TSO internal consideration |  |  | The fault recording equipment shall trigger for the measured values when exceeding the limits imposed by the following settings: - Voltage: [0.8Un, 1.2Un] V; - Active power: [-1.5Pmax, +1.5Pmax] MW; - Reactive power: [-1.5Qmax, +1.5Qmax] MVAr; - Frequency: monitoring limits [45, 55] Hz, triggering for variations more Δf = ± 200 Hz; Other triggering criteria are based on the pick-up of the overcurrent protection function (51, 51N). The required sampling rate shall be greater or at least equal to 1000 Hz. | 3 - selected for approval |  |  |  |  | studies undergoing | 1 - TSO internal consideration | project specific req. | 1 - TSO internal consideration
|  |  | 15.6.b.(iii) | RSO TSO |  |  | X | X | specifications of the oscillation trigger detecting poorly damped power oscillations |  | 1 - TSO internal consideration |  |  |  |  | Depending on the specific case |  |  | 1 - TSO internal consideration |  |  |  |  | to be defined project-specific |  | to be defined |  |  |  | n/a | [9 empty] | Project specific, based on specific analysis. |  |  | Site - specific | 1 - TSO internal consideration | [7 empty] | 1 - TSO internal consideration | [8 empty] | Case specific, but subject to national guidelines. 14.6.b.(iii) is considered exhaustive | 2a - preliminary: shared with stakeholders, but not publicly available | Monitoring oscillation with frequency range <0,1Hz; 5Hz> with thresholds activated monitoring oscillation : a) Amplitude of oscillation -Arms >2% Arms=Amplitude of oscillation/ generation’s Active Power b) damping factor x<5% x=(A1-A2)/A1, Where: A1, A2- Subsequent oscillation amplitudes | 1 - TSO internal consideration |  |  | No specific trigger required. In order to detect poorly damped power oscillation the above mentioned recorded data are used within an offline analysis. | 3 - selected for approval |  |  |  |  | studies undergoing | 1 - TSO internal consideration | tbc
|  |  | 15.6.b.(iv) | RSO PGFO TSO |  |  | X | X | protocols for recorded data. |  | 1 - TSO internal consideration |  |  |  |  | Depending on the specific case |  |  | 1 - TSO internal consideration |  |  |  |  | to be defined project-specific |  | to be defined |  |  |  | n/a | [9 empty] | Communication protocols defined in a connection agreement according to TSO and DSO technical standards. In general, all recorded data have to be stored at least 30 days. |  |  | EirGrid and Soni standards | 1 - TSO internal consideration | [7 empty] | 1 - TSO internal consideration | [8 empty] | Case specific, but subject to national guidelines. 14.6.b.(iv) is considered exhaustive | 2a - preliminary: shared with stakeholders, but not publicly available | to be defined project-specific | 1 - TSO internal consideration |  |  | The standard that should be accomplished for recorded data needs to be IEEE C37.111 and the data should be generated as “comtrade” files. The data will be accessed locally and only on demand | 3 - selected for approval |  |  |  |  | studies undergoing | 1 - TSO internal consideration | project specific req. | 1 - TSO internal consideration
| SIMULATION MODELS | X | 15.6.c.(iii) | RSO TSO |  |  |  |  | specifications of the simulation models |  | 1 - TSO internal consideration |  |  |  |  | n/a |  |  | 1 - TSO internal consideration |  |  |  |  | under discussion |  | Reusage of current requirement. Pn >10 MW |  |  |  | additionally to the compliance models, it is required the simulation for studies (defined in PO 9, already in force) | 2b - preliminary: shared with stakeholders and publicly available |  |  | under discussion | [5 empty] | PPM type D have to deliver complete dynamic model to the TSO. Other PGM should deliver simulation models upon request by TSO or DSO. Preferred PSS/E format. |  |  | In line with existing Grid Code requirement modifcation | [8 empty] | 1 - TSO internal consideration | [8 empty] | Case specific, but subject to national guidelines. 14.6.b.(iv) is considered exhaustive | 2a - preliminary: shared with stakeholders, but not publicly available | under discussion |  |  |  | Dynamics models for stability studies for voltage regulator, governer, power system stabilizer etc. in Eurostag, PSSE or Mathlab tools formats. | 3 - selected for approval |  |  |  |  | Waiting for the results of Compliance Monitoring Expert Group | 0 - no consideration | tbc
| SYNCHRONISATION |  | 16.4 | RSO PGFO |  |  |  | X | settings of the synchronisation devices |  | 1 - TSO internal consideration |  |  |  |  | ΔU≤10%;Δf≤0,05 Hz; Δᵠ≤20° | 2a - preliminary: shared with stakeholders, but not publicly available |  | 1 - TSO internal consideration |  |  |  |  | to be defined project-specific |  | to be defined |  |  |  | n/a | [9 empty] | All connection points have to be equipped with synchronisation devices including synchro-check relay. Synchronisation should be automatic and manual. Synchro-check relay determine difference between voltages, frequencies and phase angles. SETTINGS: Δf ≤ 200 mHz, Δangle ≤ 30⁰, ΔU ≤ 20 kV |  |  | Site-specifc | 1 - TSO internal consideration | [7 empty] | 1 - TSO internal consideration | [8 empty] | Case specific, but subject to national guidelines. 16.4 is considered exhaustive | 2a - preliminary: shared with stakeholders, but not publicly available | voltage range –range (-5%; +10%); frequency -smaller than 3% nominal frequency; phase angle range - range (-5°; +10°); phase sequence; - check before synchronization; deviation of voltage and frequency – according to Art. 13.1 (a) for frequency range and Art. 16.2 (a) for voltage range | 1 - TSO internal consideration |  |  | voltage range - +/-10%Un (la borne) frequency range – (47,5÷51) Hz angle less than 10°, correct phase sequence voltage difference less than 10% Un frequency difference less than 50 mHz. ” | 3 - selected for approval |  |  |  |  | studies undergoing | 1 - TSO internal consideration | project specific req. | 1 - TSO internal consideration
| SYNTHETIC INERTIA CAPABILITY FOR PPM | X | 21.2 | TSO |  |  | X | X | definition of the operating principle of control systems to provide synthetic inertia and the related performance parameters |  | 1 - TSO internal consideration |  |  |  |  | n/a |  |  | 1 - TSO internal consideration | [5 empty] | 0 - no consideration | considering planning of workshop |  |  |  | some requirements defined | 2b - preliminary: shared with stakeholders and publicly available |  |  |  | 0 - no consideration |  |  |  |  | Waiting for European coordination |  |  | N/A as not being mandated - review in 3 years | 1 - TSO internal consideration | [7 empty] | 1 - TSO internal consideration | [8 empty] | Case specific, but subject to national guidelines. 21.2 is considered exhaustive | 2a - preliminary: shared with stakeholders, but not publicly available | n/a |  |  |  |  | 1 - TSO internal consideration |  |  |  |  | Waiting for European coordination | 0 - no consideration | n/a | 0 - no consideration
[63 empty] | n/a |  |  |  | We do not know any requirement. | [5 empty] | Waiting for European coordination | 0 - no consideration | n/a

## Parameters (hidden)
0 - no consideration
1 - TSO internal consideration
2a - preliminary: shared with stakeholders, but not publicly available
2b - preliminary: shared with stakeholders and publicly available
3 - selected for approval
4 - approved/binding