## Informacije
Pomoćna usluga | Naziv informacije | Izvor informacije | Razina | Informacija | Tip informacije | IEC 104 ASDU tip | ASDU adresa | IOA | Točnost mjerenja | Prijenos | Opis
mFRR | REZERVA SNAGE | PRUŽATELJ USLUGE URAVNOTEŽENJA | PORTFELJ ili grupa | Mjerenje | Measured Value (MW) | M_ME_NC_1 |  |  | klasa točnosti 0.5 (izvorišni uređaj) | Periodički 2sek bez mrtve zone | Trenutna rezerva snage (ukupna fleksibilnost) u portfelju ili grupi (uključuje dobrovoljnu rezervu). Pružatelj treba slati odvojene signale za mFRR- i mFRR+ grupe i aFRR+ i aFRR- grupe.
mFRR | REGULACIJSKA RADNA SNAGA | PRUŽATELJ USLUGE URAVNOTEŽENJA | PORTFELJ ili GRUPA | Mjerenje | Measured Value (MW) | M_ME_NC_1 |  |  | klasa točnosti 0.5 (izvorišni uređaj) | Periodički 2sek bez mrtve zone | Trenutna mjerena radna snaga portfelja ili grupe u regulaciji. Pružatelj treba slati odvojene signale za mFRR- i mFRR+ grupe i aFRR+ i aFRR- grupe.
mFRR | PLANIRANA BAZNA SNAGA 5-MIN UNAPRIJED | PRUŽATELJ USLUGE URAVNOTEŽENJA | PORTFELJ ili GRUPA | Mjerenje | Measured Value (MW) | M_ME_NC_1 |  |  | klasa točnosti 0.5 (izvorišni uređaj) | Periodički 2sek bez mrtve zone | Planirana bazna snaga portfelja ili grupe za 5-min unaprijed. Pružatelj treba slati odvojene signale za mFRR- i mFRR+ grupe i aFRR+ i aFRR- grupe..
mFRR | TRENUTNA RADNA SNAGA (JEDINICA n) | PRUŽATELJ USLUGE URAVNOTEŽENJA | JEDINICA | Mjerenje | Measured Value (MW) | M_ME_NC_1 |  |  | klasa točnosti 0.5 (izvorišni uređaj) | Periodički 2sek bez mrtve zone | Trenutna radna snaga pojedine jedinice (ako je >1,5 MW)
mFRR | PLANIRANA BAZNA SNAGA 5-MIN UNAPRIJED (JEDINICA n) | PRUŽATELJ USLUGE URAVNOTEŽENJA | JEDINICA | Mjerenje | Measured Value (MW) | M_ME_NC_1 |  |  | klasa točnosti 0.5 (izvorišni uređaj) | Periodički 2sek bez mrtve zone | Planirana bazna snaga pojedine jedinice za 5-min unaprijed (ako je >1,5 MW)
mFRR/aFRR | TRENUTNA RADNA SNAGA (TEST 1) | PRUŽATELJ USLUGE URAVNOTEŽENJA | JEDINICA | Mjerenje | Measured Value (MW) | M_ME_NC_1 |  |  | klasa točnosti 0.5 (izvorišni uređaj) | Periodički 2sek bez mrtve zone | Trenutna radna snaga pojedine jedinice ili grupe nominirane za pretkvalifikaciju (ako je >1,5 MW)
mFRR/aFRR | PLANIRANA BAZNA SNAGA 5-MIN UNAPRIJED (TEST 1) | PRUŽATELJ USLUGE URAVNOTEŽENJA | JEDINICA | Mjerenje | Measured Value (MW) | M_ME_NC_1 |  |  | klasa točnosti 0.5 (izvorišni uređaj) | Periodički 2sek bez mrtve zone | Planirana bazna snaga pojedine jedinice ili grupe nominirane za pretkvalifikaciju za 5-min unaprijed (ako je >1,5 MW)
mFRR/aFRR | TRENUTNA RADNA SNAGA (TEST 2) | PRUŽATELJ USLUGE URAVNOTEŽENJA | JEDINICA | Mjerenje | Measured Value (MW) | M_ME_NC_1 |  |  | klasa točnosti 0.5 (izvorišni uređaj) | Periodički 2sek bez mrtve zone | Trenutna radna snaga pojedine jedinice ili grupe nominirane za pretkvalifikaciju (ako je >1,5 MW)
mFRR/aFRR | PLANIRANA BAZNA SNAGA 5-MIN UNAPRIJED (TEST 2) | PRUŽATELJ USLUGE URAVNOTEŽENJA | JEDINICA | Mjerenje | Measured Value (MW) | M_ME_NC_1 |  |  | klasa točnosti 0.5 (izvorišni uređaj) | Periodički 2sek bez mrtve zone | Planirana bazna snaga pojedine jedinice ili grupe nominirane za pretkvalifikaciju za 5-min unaprijed (ako je >1,5 MW)
aFRR | ZAHTIJEVANA SNAGA (TEST 1) | HOPS | PORTFELJ ili GRUPA | Nalog | Setpoint Command (MW) Resolution up to 1 decimal | C_SE_NC_1 |  |  |  |  | Nalog s postavnom vrijednošću zahtijevane radne snage portfelja ili grupe jedinica. U slučaju grupe jedinica, šalje se signal za svaku pojedinu grupu.
aFRR | REGULACIJSKA RADNA SNAGA | PRUŽATELJ USLUGE URAVNOTEŽENJA | PORTFELJ ili GRUPA | Mjerenje | Measured Value (MW) | M_ME_NC_1 |  |  | klasa točnosti 0.5 (izvorišni uređaj) | Periodički 2sek bez mrtve zone | Trenutna mjerena radna snaga portfelja ili grupe jedinica koji sudjeluju u regulaciji. Pružatelj treba slati odvojene signale za aFRR+ i aFRR- grupe.
aFRR | PLANIRANA BAZNA SNAGA 5-MIN UNAPRIJED | PRUŽATELJ USLUGE URAVNOTEŽENJA | PORTFELJ ili GRUPA ili JEDINICA | Mjerenje | Measured Value (MW) | M_ME_NC_1 |  |  | klasa točnosti 0.5 (izvorišni uređaj) | Periodički 2sek bez mrtve zone | Planirana bazna snaga portfelja ili grupe ili jedinice za 5-min unaprijed. U slučaju grupe jedinica, šalje se signal za svaku pojedinu grupu. Pružatelj treba slati odvojene signale za aFRR+ i aFRR- grupe.
aFRR | GORNJA GRANICA OPSEGA REGULACIJE | PRUŽATELJ USLUGE URAVNOTEŽENJA | PORTFELJ ili GRUPA | Mjerenje | Measured Value (MW) | M_ME_NC_1 |  |  |  | Spontano bez mrtve zone | Trenutna gornja granica opsega portfelja ili grupe jedinica koji sudjeluju u regulaciji za trenutni interval (15 min od 2024. godine). Pružatelj treba slati odvojene signale za aFRR+ i aFRR- grupe.
aFRR | DONJA GRANICA OPSEGA REGULACIJE | PRUŽATELJ USLUGE URAVNOTEŽENJA | PORTFELJ ili GRUPA | Mjerenje | Measured Value (MW) | M_ME_NC_1 |  |  |  | Spontano bez mrtve zone | Trenutna donja granica opsega portfelja ili grupe jedinica koji sudjeluju u regulaciji za trenutni interval (15 min od 2024. godine). U slučaju grupe jedinica, šalje se signal za svaku pojedinu grupu.
aFRR | SEKUNDARNA REGULACIJA AKTIVNA | HOPS | PORTFELJ ili GRUPA ili JEDINICA | Nalog | Single Command {0 - ISK , 1 - UK} | C_SC_NA_1 |  |  |  |  | Signal iz HOPS-a koji ukazuje da se portfelj ili grupa ili jedinica trenutno koristi za sekundarnu regulaciju. Pružatelj treba slati odvojene signale za aFRR+ i aFRR- grupe.
aFRR | SEKUNDARNA REGULACIJA AKTIVNA | PRUŽATELJ USLUGE URAVNOTEŽENJA | PORTFELJ ili GRUPA ili JEDINICA | Indikacija | Single Point Information {0 - ISK , 1 - UK} | M_SP_NA_1 |  |  |  |  | Signal od strane pružatelja usluge koji ukazuje da portfelj ili grupa ili jedinica trenutno sudjeluje u sekundarnoj regulaciji. Pružatelj treba slati odvojene signale za aFRR+ i aFRR- grupe.
aFRR | ZAHTIJEVANA SNAGA | HOPS | PORTFELJ ili GRUPA | Nalog | Setpoint Command (MW) Resolution up to 1 decimal | C_SE_NC_1 |  |  |  |  | Nalog s postavnom vrijednošću zahtijevane radne snage portfelja ili grupe jedinica. Pružatelj treba slati odvojene signale za aFRR+ i aFRR- grupe.
aFRR | ZAPRIMLJENA ZAHTIJEVANA SNAGA | PRUŽATELJ USLUGE URAVNOTEŽENJA | PORTFELJ ili GRUPA | Mjerenje | Measured Value (MW) | M_ME_NC_1 |  |  |  |  | Potvda zaprimljenog naloga s postavnom vrijednošću zahtijevane radne snage portfelja ili grupe jedinica. Pružatelj treba slati odvojene signale za aFRR+ i aFRR- grupe.
aFRR | PING | PRUŽATELJ USLUGE URAVNOTEŽENJA | N/A | Mjerenja | Analog Counter Value | M_ME_NC_1 |  |  |  |  | OPCIONALNO! Periodička poruka koja se šalje iz elektrane radi provjere ispravnosti komunikacije u stvarnom vremenu s HOPS-om. Svaka PING poruka zahtijeva odgovor partnerskog sustava u obliku PONG poruke s istom vrijednošću. PING vrijednost se uvećava ili smanjuje za 1 u rasponu od 0 do 1000.
aFRR | PONG | HOPS | N/A | Nalog | Setpoint Command | C_SE_NC_1 |  |  |  |  | OPCIONALNO! Odgovor iz HOPS-a na periodičku PING poruku dobivenu iz elektrane s istom vrijednošću kao onom dobivenom kroz PING porukom.
aFRR | TRENUTNA RADNA SNAGA (JEDINICA n) | PRUŽATELJ USLUGE URAVNOTEŽENJA | JEDINICA | Mjerenje | Measured Value (MW) | M_ME_NC_1 |  |  | klasa točnosti 0.5 (izvorišni uređaj) | Periodički 2sek bez mrtve zone | Trenutna radna snaga pojedine jedinice (ako je >1,5 MW)
aFRR | FREKVENCIJA (JEDINICA n) | PRUŽATELJ USLUGE URAVNOTEŽENJA | JEDINICA | Mjerenje | Measured Value (MW) | M_ME_NC_1 |  |  | klasa točnosti 0.5 (izvorišni uređaj) | 1mHz | Trenutna frekvencija pojedine jedinice (ako je >1,5 MW) OPCIONALNO! Za jedinice spojene na ODS-u OBAVEZNO! Za jedinice spojene na prijenosnu mrežu
aFRR | PLANIRANA BAZNA SNAGA 5-MIN UNAPRIJED (JEDINICA n) | PRUŽATELJ USLUGE URAVNOTEŽENJA | JEDINICA | Mjerenje | Measured Value (MW) | M_ME_NC_1 |  |  | klasa točnosti 0.5 (izvorišni uređaj) | Periodički 2sek bez mrtve zone | Planirana bazna snaga pojedine jedinice za 5-min unaprijed (ako je >1,5 MW)

## Data points
Ancillary Service | Information Name | Information Source | Level | Information | Information Type | IEC 104 ASDU type | ASDU address | IOA | Measurement accuracy | Transmission | Description
mFRR | POWER RESERVE | BALANCING SERVICE PROVIDER | PORTFOLIO or GROUP | Mjerenje | Measured Value (MW) | M_ME_NC_1 |  |  | accuracy class 0.5 (source device) | Periodic 2sec without dead zone | Current power reserve (total flexibility) in the portfolio or group (includes voluntary reserve). The provider should send separate signals for mFRR- and mFRR+ groups and aFRR+ i aFRR- groups.
mFRR | CURRENT ACTIVE POWER | BALANCING SERVICE PROVIDER | PORTFOLIO or GROUP | Measurement | Measured Value (MW) | M_ME_NC_1 |  |  | accuracy class 0.5 (source device) | Periodic 2sec without dead zone | Current active power of aggregated portfolio or group. The provider should send separate signals for mFRR- and mFRR+ groups and aFRR+ i aFRR- groups.
mFRR | 5-MIN BASELINE CALCULATION | BALANCING SERVICE PROVIDER | PORTFOLIO or GROUP | Measurement | Measured Value (MW) | M_ME_NC_1 |  |  | accuracy class 0.5 (source device) | Periodic 2sec without dead zone | 5 minute baseline prognosis for aggregated portfolio. The provider should send separate signals for mFRR- and mFRR+ groups and aFRR+ i aFRR- groups.
mFRR | CURRENT ACTIVE POWER (UNIT n) | BALANCING SERVICE PROVIDER | UNIT | Measurement | Measured Value (MW) | M_ME_NC_1 |  |  | accuracy class 0.5 (source device) | Periodic 2sec without dead zone | Current active power of individual unit (if >1,5 MW)
mFRR | 5-MIN BASELINE CALCULATION (UNIT n) | BALANCING SERVICE PROVIDER | UNIT | Measurement | Measured Value (MW) | M_ME_NC_1 |  |  | accuracy class 0.5 (source device) | Periodic 2sec without dead zone | 5 minute baseline prognosis for individual unit (if >1,5 MW)
mFRR/aFRR | CURRENT ACTIVE POWER (TEST 1) | BALANCING SERVICE PROVIDER | UNIT | Measurement | Measured Value (MW) | M_ME_NC_1 |  |  | accuracy class 0.5 (source device) | Periodic 2sec without dead zone | Current active power of individual unit or group submitted for prequalification (if <1,5 MW)
mFRR/aFRR | 5-MIN BASELINE CALCULATION (TEST 1) | BALANCING SERVICE PROVIDER | UNIT | Measurement | Measured Value (MW) | M_ME_NC_1 |  |  | accuracy class 0.5 (source device) | Periodic 2sec without dead zone | 5 minute baseline prognosis for individual unit or group submitted for prequalification (if <1,5 MW)
mFRR/aFRR | CURRENT ACTIVE POWER (TEST 2) | BALANCING SERVICE PROVIDER | UNIT | Measurement | Measured Value (MW) | M_ME_NC_1 |  |  | accuracy class 0.5 (source device) | Periodic 2sec without dead zone | Current active power of individual unit or group submitted for prequalification (if <1,5 MW)
mFRR/aFRR | 5-MIN BASELINE CALCULATION (TEST 2) | BALANCING SERVICE PROVIDER | UNIT | Measurement | Measured Value (MW) | M_ME_NC_1 |  |  | accuracy class 0.5 (source device) | Periodic 2sec without dead zone | 5 minute baseline prognosis for individual unit or group submitted for prequalification (if <1,5 MW)
aFRR | ACTIVE POWER SETPOINT (TEST 1) | HOPS | PORTFOLIO or GROUP | Control | Setpoint Command (MW) Resolution up to 1 decimal | C_SE_NC_1 |  |  |  |  | Setpoint command with requested active power value of aggregated portfolio or group of units. In case of group of units, setpoints are sent for each one of them.
aFRR | CURRENT ACTIVE POWER | BALANCING SERVICE PROVIDER | PORTFOLIO or GROUP or UNIT | Measurement | Measured Value (MW) | M_ME_NC_1 |  |  | accuracy class 0.5 (source device) | Periodic 2sec without dead zone | Current active power of aggregated portfolio or group of units. The provider should send separate signals for aFRR+ i aFRR- groups.
aFRR | 5-MIN BASELINE CALCULATION | BALANCING SERVICE PROVIDER | PORTFOLIO or GROUP or UNIT | Measurement | Measured Value (MW) | M_ME_NC_1 |  |  | accuracy class 0.5 (source device) | Periodic 2sec without dead zone | 5 minute baseline prognosis for aggregated portfolio or group of units. The provider should send separate signals for aFRR+ i aFRR- groups.
aFRR | ACTIVE POWER LIMIT HIGH | BALANCING SERVICE PROVIDER | PORTFOLIO or GROUP | Measurement | Measured Value (MW) | M_ME_NC_1 |  |  |  | Spontaneous without dead zone | Highest active power of aggregated portfolio or group of units available for secondary regulation in current interval (15 min as of 2024). The provider should send separate signals for aFRR+ i aFRR- groups.
aFRR | ACTIVE POWER LIMIT LOW | BALANCING SERVICE PROVIDER | PORTFOLIO or GROUP | Measurement | Measured Value (MW) | M_ME_NC_1 |  |  |  | Spontaneous without dead zone | Lowest active power of aggregated portfolio or group of units available for secondary regulation in current interval (15 min as of 2024). The provider should send separate signals for aFRR+ i aFRR- groups.
aFRR | SECONDARY REGULATION ACTIVE | HOPS | PORTFOLIO or GROUP or UNITS | Control | Single Command {0 - ISK , 1 - UK} | C_SC_NA_1 |  |  |  |  | Signal sent from HOPS indicating that aggregated portfolio or group of units is currently being used for secondary regulation. The provider should send separate signals for aFRR+ i aFRR- groups.
aFRR | SECONDARY REGULATION ACTIVE | BALANCING SERVICE PROVIDER | PORTFOLIO or GROUP or UNITS | Indication | Single Point Information {0 - ISK , 1 - UK} | M_SP_NA_1 |  |  |  |  | Signal sent from BSP indicating that aggregated portfolio or group of units is currently being used for secondary regulation. The provider should send separate signals for aFRR+ i aFRR- groups.
aFRR | ACTIVE POWER SETPOINT | HOPS | PORTFOLIO or GROUP | Control | Setpoint Command (MW) Resolution up to 1 decimal | C_SE_NC_1 |  |  |  |  | Setpoint command with requested active power value of aggregated portfolio or group of units. The provider should send separate signals for aFRR+ i aFRR- groups.
aFRR | RECEIVED ACTIVE POWER SETPOINT | BALANCING SERVICE PROVIDER | PORTFOLIO or GROUP | Measurement | Measured Value (MW) | M_ME_NC_1 |  |  |  |  | Last active power setpoint value send by HOPS and received by provider. The provider should send separate signals for aFRR+ i aFRR- groups.
aFRR | PING | BALANCING SERVICE PROVIDER | N/A | Measurement | Analog Counter Value | M_ME_NC_1 |  |  |  |  | OPTIONAL! Periodic message sent from ancillary service provider to verify proper functioning of real time comunication with HOPS. Each PING message requires response from partner system in the form of PONG message with the same value. PING value is incremented or decremented by 1 in the range od 0 to 1000.
aFRR | PONG | HOPS | N/A | Control | Setpoint Command | C_SE_NC_1 |  |  |  |  | OPTIONAL! Response from HOPS to periodic PING message sent by the ancillary service provider with the same value as received through PING message.
aFRR | CURRENT ACTIVE POWER (UNIT n) | BALANCING SERVICE PROVIDER | UNIT | Measurement | Measured Value (MW) | M_ME_NC_1 |  |  | accuracy class 0.5 (source device) | Periodic 2sec without dead zone | Current active power of each individual unit >1,5 MW
aFRR | FREQUENCY (UNIT n) | BALANCING SERVICE PROVIDER | UNIT | Measurement | Measured Value (MW) | M_ME_NC_1 |  |  | accuracy class 0.5 (source device) | 1mHz | Current frequency measurement of each individual unit >1,5 MW OPTIONAL! For units connected on distribution grid MANDATORY! For units connected on transsmission grid
aFRR | 5-MIN BASELINE CALCULATION (UNIT n) | BALANCING SERVICE PROVIDER | UNIT | Measurement | Measured Value (MW) | M_ME_NC_1 |  |  | accuracy class 0.5 (source device) | Periodic 2sec without dead zone | 5 minute baseline prognosis for each individual unit >1,5 MW)