## UE 2016_1447_LoRI_TSO (HVDC)
GENERAL REQUIREMENTS FOR HVDC CONNECTIONS
Implementation in Member State
Aspect | Non-Exhaustive Requirement | Non-Mandatory Requirement | Article | Definition | Comment | Defined values or specifications for the requirement to be implemented | State of implementation | AT | BA | BE | BG | CH | CY | CZ | DE | DK | EE | ES | FI | FR | GB | GR | HR | HU | IE | IS | IT | LT | LU | LV | ME | MK | NL | NO | PL | PT | RO | RS | SE | SI | SK | AT |  | BA |  | BE |  | BG |  | CH |  | CY |  | CZ |  | DE |  | DK |  | EE |  | ES |  | FI |  | FR |  | GB |  | GR |  | HR
| NA |  |  | RSO/TSO | Proposal of requirements of general applications |  |  | Implementation in Member State AT: Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status
FREQUENCY RELATED PARAMETERS | FREQUENCY RANGES |  | 11.1 | TSO | Time period for operation in the frequency ranges (According to Table 1, Annex I) 47.0 Hz - 47.5 Hz 47.5 Hz - 48.5 Hz 48.5 Hz - 49.0 Hz 49.0 Hz - 51.0 Hz 51.0 Hz - 51.5 Hz 51.5 Hz - 52.0 Hz | [40 empty] | 47.0 Hz to 47.5 Hz: 60 seconds 47,5 Hz – 48,5 Hz: Unlimited 48,5 Hz – 49,0 Hz: Unlimited 49,0 Hz – 51,0 Hz Unlimited | 1 - TSO internal consideration | [24 empty] | 47.0 Hz to 47.5 Hz: Min. 60 seconds 47.5 Hz – 48.5 Hz: Min. 90 minutes 48.5 Hz – 49.0 Hz: Min. 90 minutes 49.0 Hz – 51.0 Hz: Unlimited 51.0 Hz - 51.5 Hz: Min. 90 minutes 51.5 Hz - 52.0 Hz: Min. 15 minutes | 1 - TSO internal consideration
|  |  | 11.3 | TSO | Automatic disconnection at specifed frequencies | [40 empty] | In case of frequency deviations, the Interconnector may disconnect only to protect the equipment, and in no case within the range 47.5 Hz to 52.5 Hz | 1 - TSO internal consideration | [24 empty] | Site specific requirement. | 1 - TSO internal consideration
|  | x | 11.4 | TSO | Maximum admissible active power output reduction from its operating point if the system frequency falls below 49 Hz. | [40 empty] | When operating at an AC system frequency below 49 Hz, the maximum active power shall not be reduced beyond 2%/Hz. | 1 - TSO internal consideration | [24 empty] | Equal to Type D PGMs. Maximum output reduction is 10% in range from 49.0 Hz to 47.5 Hz (10% Pmax / 1.5 Hz = 6,67% Pmax / Hz ). | 1 - TSO internal consideration
| RATE-OF-CHANGE-OF-FREQUENCY WITHSTAND CAPABILITY |  | 12 | HVDC | An HVDC system shall be capable of staying connected to the network and operable if the network frequency changes at a rate between – 2,5 and + 2,5 Hz/s (measured at any point in time as an average of the rate of change of frequency for the previous 1 s). | [40 empty] | Exhaustive requirement | 0 - no consideration | [24 empty] | Exhaustive requirement. | 0 - no consideration
| ACTIVE POWER CONTROLLABILITY, CONTROL RANGE AND RAMPING RATE |  | 13.1.a | TSO | an HVDC system shall be capable of adjusting the transmitted active power up to its maximum HVDC active power transmission capacity in each direction following an instruction from the relevant TSO. Maximum active power capacity, step size, minimum active power capacity, and delay before adjustment of the transmitted power | [40 empty] | It shall be possible to refresh the active power setpoint every second. The power step size for adjusting the transmitted active power shall be at least 1 MW. | 1 - TSO internal consideration | [24 empty] | Minimum the capability required for Type D PGMs. Maximum delay for adjusting the transmitted active power upon TSO request is 1 minute. | 1 - TSO internal consideration
|  |  | 13.1.b | TSO | the relevant TSO shall specify how an HVDC system shall be capable of modifying the transmitted active power infeed in case of disturbances into one or more of the AC networks to which it is connected. If the initial delay prior to the start of the change is greater than 10 milliseconds from receiving the triggering signal sent by the relevant TSO, it shall be reasonably justified by the HVDC system owner to the relevant TSO. | [40 empty] | Site specific | [25 empty] | Site specific requirement. | 1 - TSO internal consideration
|  | x | 13.1.c | TSO | the relevant TSO may specify that an HVDC system be capable of fast active power reversal. The power reversal shall be possible from the maximum active power transmission capacity in one direction to the maximum active power transmission capacity in the other direction as fast as technically feasible and reasonably justified by the HVDC system owner to the relevant TSOs if greater than 2 seconds. | [40 empty] | Site specific | [25 empty] | Site specific requirement. | 1 - TSO internal consideration
|  |  | 13.1.d | TSO | for HVDC systems linking various control areas or synchronous areas, the HVDC system shall be equipped with control functions enabling the relevant TSOs to modify the transmitted active power for the purpose of cross-border balancing. | [40 empty] | Site specific | [25 empty] | Exhaustive requirement | 0 - no consideration
|  |  | 13.2 | TSO | An HVDC system shall be capable of adjusting the ramping rate of active power variations within its technical capabilities in accordance with instructions sent by relevant TSOs. In case of modification of active power according to points (b) and (c) of paragraph 1, there shall be no adjustment of ramping rate. | [40 empty] | Exhaustive requirement | [25 empty] | Exhaustive requirement | 0 - no consideration
|  |  | 13.3 | TSO | Trigger and blocking criteria for automatic responses | [40 empty] | Site specific | [25 empty] | Site specific requirement. | 1 - TSO internal consideration
| SYNTHETIC INERTIA | X | 14.1 | TSO | If specified by a relevant TSO, an HVDC system shall be capable of providing synthetic inertia in response to frequency changes, activated in low and/or high frequency regimes by rapidly adjusting the active power injected to or withdrawn from the AC network in order to limit the rate of change of frequency. The requirement shall at least take account of the results of the studies undertaken by TSOs to identify if there is a need to set out minimum inertia. | [41 empty] | 0 - no consideration | [24 empty] | Waiting for ENTSO-E coordination for Continental Europe. | 1 - TSO internal consideration
| FREQUENCY SENSITIVE MODE |  | 15 | TSO | Requirements applying to frequency sensitive mode, limited frequency sensitive mode overfrequency and limited frequency sensitive mode underfrequency shall be as set out in Annex II. | [40 empty] | Alligned with RfG requirements | [25 empty] | As defined in Annex II and coordinated with RfG requirements (Type D PGMs). FSM Frequency response deadband: ± 20 mHz Droop s1: initial 5% (range 2% - 12%) Droop s2: initial 5% (range 2% - 12%) Frequency response insensitivity: 10 mHz Maximum admissible initial delay t1: 0,5 seconds Maximum admissible time for full activation t2: 30 seconds LFSM-O Frequency threshold f1: 50,2 Hz Droop s3: initial 5% (range 2% - 12%) LFSM-U Frequency threshold f2: 49,8 Hz Droop s4: initial 5% (range 2% - 12%) | 1 - TSO internal consideration
VOLTAGE RELATED PARAMETERS | VOLTAGE RANGE |  | 18.1 | TSO, adjacent RSOs | Without prejudice to Article 25, an HVDC converter station shall be capable of staying connected to the network and capable of operating at HVDC system maximum current, within the ranges of the network voltage at the connection point, expressed by the voltage at the connection point related to reference 1 pu voltage, and the time periods specified in Tables 4 and 5, Annex III. The establishment of the reference 1 pu voltage shall be subject to coordination between the adjacent relevant system operators. | [66 empty] | Minimum the duration required for Type D PGMs. 110 kV ≤ Un < 300 kV 0,85 pu - 1,118 pu: Unlimited 1,118 pu - 1,15 pu: Min. 60 minutes 300 kV < Un ≤ 400 kV 0,85 pu - 1,05 pu: Unlimited 1,05 pu - 1,0875 pu: Min. 60 minutes 1,0875 pu - 1,10 pu: Min. 60 minutes | 1 - TSO internal consideration
|  |  | 18.4 | RSO/RTSO's | For connection points at reference 1 pu AC voltages not included in the scope set out in Annex III, the relevant system operator, in coordination with relevant TSOs, shall specify applicable requirements at the connection points. | [66 empty] | Site specific requirement. | 1 - TSO internal consideration
|  |  | 18.5 | RTSO's | Notwithstanding the provisions of paragraph 1, the relevant TSOs in the Baltic synchronous area may, following consultation with relevant neighbouring TSOs, require HVDC converter stations to remain connected to the 400 kV network in the voltage ranges and for time periods that apply in the Continental Europe synchronous area. | [66 empty] | Not applicable. | 0 - no consideration
| SHORT CIRCUIT CONTRIBUTION DURING FAULTS |  | 19.1 | RSO, RTSO | If specified by the relevant system operator, in coordination with the relevant TSO, an HVDC system shall have the capability to provide fast fault current at a connection point in case of symmetrical (3-phase) faults. | [66 empty] | Equal to Type D PPMs. | 1 - TSO internal consideration
|  |  | 19.2 | RSO, RTSO | Where an HVDC system is required to have the capability referred to in paragraph 1, the relevant system operator, in coordination with the relevant TSO, shall specify the following: (a) how and when a voltage deviation is to be determined as well as the end of the voltage deviation; (b) the characteristics of the fast fault current; (c) the timing and accuracy of the fast fault current, which may include several stages. | [66 empty] | Equal to Type D PPMs. | 1 - TSO internal consideration
|  |  | 19.3 | RSO, RTSO | The relevant system operator, in coordination the relevant TSO, may specify a requirement for asymmetrical current injection in the case of asymmetrical (1-phase or 2-phase) faults. | [66 empty] | Equal to Type D PPMs. | 1 - TSO internal consideration
| REACTIVE POWER CAPABILITY |  | 20.1 | RSO, RTSO | The relevant system operator, in coordination with the relevant TSO, shall specify the reactive power capability requirements at the connection points, in the context of varying voltage. The proposal for those requirements shall include a U-Q/Pmax-profile, within the boundary of which the HVDC converter station shall be capable of providing reactive power at its maximum HVDC active power transmission capacity. | [66 empty] | Not less requirements than Type D PGMs. Voltage-against-power factor profile: Q/Pmax ±0,33 for voltage range 0,85-1,15 pu | 1 - TSO internal consideration
|  |  | 20.3 |  | An HVDC system shall be capable of moving to any operating point within its U-Q/Pmax profile in timescales specified by the relevant system operator in coordination with the relevant TSO. | [66 empty] | Not less requirements than Type D PGMs. 1 minute upon TSO request. | 1 - TSO internal consideration
|  |  | 20.4 |  | When operating at an active power output below the maximum HVDC active power transmission capacity (P < Pmax), the HVDC converter station shall be capable of operating in every possible operating point, as specified by the relevant system operator in coordination with the relevant TSO and in accordance with the reactive power capability set out by the U-Q/Pmax profile specified in paragraphs 1 to 3. | [66 empty] | Not less requirements than Type D PGMs. | 1 - TSO internal consideration
| REACTIVE POWER EXCHANGED WITH THE NETWORK |  | 21.1 | RSO,RTSO | The HVDC system owner shall ensure that the reactive power of its HVDC converter station exchanged with the network at the connection point is limited to values specified by the relevant system operator in coordination with the relevant TSO. | [66 empty] | Equal to Type D PGMs. Power factor ≥ 0,95 pu (lead, lag). | 1 - TSO internal consideration
|  |  | 21.2 | RSO,RTSO | The reactive power variation caused by the reactive power control mode operation of the HVDC converter Station, referred to in Article 22(1), shall not result in a voltage step exceeding the allowed value at the connection point. The relevant system operator, in coordination with the relevant TSO, shall specify this maximum tolerable voltage step value. | [66 empty] | Equal to Type D PGMs. Voltage change ≤ 5% / minute. | 1 - TSO internal consideration
| REACTIVE POWER CONTROL MODE |  | 22.1 |  | An HVDC converter station shall be capable of operating in one or more of the three following control modes, as specified by the relevant system operator in coordination with the relevant TSO: (a) voltage control mode; (b) reactive power control mode; (c) power factor control mode. | [66 empty] | Equal to Type D PPMs. | 1 - TSO internal consideration
|  |  | 22.2 |  | An HVDC converter station shall be capable of operating in additional control modes specified by the relevant system operator in coordination with the relevant TSO. | [66 empty] | Equal to Type D PPMs. | 1 - TSO internal consideration
|  |  | 22.3 |  | For the purposes of voltage control mode, each HVDC converter station shall be capable of contributing to voltage control at the connection point utilising its capabilities, while respecting Articles 20 and 21, in accordance with the following control characteristics: (a) a setpoint voltage at the connection point shall be specified to cover a specific operation range, either continuously or in steps, by the relevant system operator, in coordination with the relevant TSO; (b) the voltage control may be operated with or without a deadband around the setpoint selectable in a range from zero to +/– 5 % of reference 1 pu network voltage. The deadband shall be adjustable in steps as specified by the relevant system operator in coordination with the relevant TSO; (c) following a step change in voltage, the HVDC converter station shall be capable of: (i) achieving 90 % of the change in reactive power output within a time t1 specified by the relevant system operator in coordination with the relevant TSO. The time t1 shall be in the range of 0,1-10 seconds; and (ii) settling at the value specified by the operating slope within a time t2 specified by the relevant system operator in coordination with the relevant TSO. The time t2 shall be in the range of 1-60 seconds, with a specified steady- state tolerance given in % of the maximum reactive power. (d) voltage control mode shall include the capability to change reactive power output based on a combination of a modified setpoint voltage and an additional instructed reactive power component. The slope shall be specified by a range and step specified by the relevant system operator in coordination with the relevant TSO. | [66 empty] | Equal to Type D PPMs. | 1 - TSO internal consideration
|  |  | 22.4 |  | With regard to reactive power control mode, the relevant system operator shall specify a reactive power range in MVAr or in % of maximum reactive power, as well as its associated accuracy at the connection point, using the capabilities of the HVDC system, while respecting Articles 20 and 21. | [66 empty] | Equal to Type D PPMs. | 1 - TSO internal consideration
|  |  | 22.5 |  | For the purposes of power factor control mode, the HVDC converter station shall be capable of controlling the power factor to a target at the connection point, while respecting Articles 20 and 21. The available setpoints shall be available in steps no greater than a maximum allowed step specified by the relevant system operator. | [66 empty] | Equal to Type D PPMs. | 1 - TSO internal consideration
|  |  | 22.6 |  | The relevant system operator in coordination with the relevant TSO shall specify any equipment needed to enable the remote selection of control modes and relevant setpoints. | [66 empty] | Equal to Type D PPMs. | 1 - TSO internal consideration
| POWER QUALITY |  | 24 | RSO,RTSO | An HVDC system owner shall ensure that its HVDC system connection to the network does not result in a level of distortion or fluctuation of the supply voltage on the network, at the connection point, exceeding the level specified by the relevant system operator in coordination with the relevant TSO. The process for necessary studies to be conducted and relevant data to be provided by all grid users involved, as well as mitigating actions identified and implemented, shall be in accordance with the process in Article 29. | [66 empty] | Equal to Type D PGMs. | 1 - TSO internal consideration
REQUIREMENTS FOR FAULT RIDE THROUGH CAPABILIGY | FAULT RIDE THROUGH CAPABILITY |  | 25.1 |  | The relevant TSO shall specify, while respecting Article 18, a voltage-against time profile as set out in Annex V and having regard to the voltage-against-time-profile specified for power park modules according to Regulation (EU) 2016/631. This profile shall apply at connection points for fault conditions, under which the HVDC converter station shall be capable of staying connected to the network and continuing stable operation after the power system has recovered following fault clearance. The voltage-against-time-profile shall express a lower limit of the actual course of the phase-to-phase voltages on the network voltage level at the connection point during a symmetrical fault, as a function of time before, during and after the fault. Any ride through period beyond trec2 shall be specified by the relevant TSO consistent with Article 18. | [66 empty] | Equal to Type D PPMs.. Voltage parameters: Urec = 0,30 pu Urec1 = 0,85 pu Urec2 = 0,90 pu Time parameters: trec = 0,25 s trec1 = 2,5 s trec2 = 10,0 s Ublock = 0,7 | 1 - TSO internal consideration
|  |  | 25.2 |  | On request by the HVDC system owner, the relevant system operator shall provide the pre-fault and post-fault conditions as provided for in Article 32 regarding: (a) pre-fault minimum short circuit capacity at each connection point expressed in MVA; (b) pre-fault operating point of the HVDC converter station expressed as active power output and reactive power output at the connection point and voltage at the connection point; and (c) post-fault minimum short circuit capacity at each connection point expressed in MVA. Alternatively, generic values for the above conditions derived from typical cases may be provided by the relevant system operator. | [66 empty] | Equal to Type D PPMs. | 1 - TSO internal consideration
|  |  | 25.3 |  | The HVDC converter station shall be capable of staying connected to the network and continue stable operation when the actual course of the phase-to-phase voltages on the network voltage level at the connection point during a symmetrical fault, given the pre-fault and post-fault conditions provided for in Article 32, remain above the lower limit set out in the figure in Annex V, unless the protection scheme for internal faults requires the disconnection of the HVDC converter station from the network. The protection schemes and settings for internal faults shall be designed not to jeopardise fault-ride-through performance. | [66 empty] | Equal to Type D PPMs. | 1 - TSO internal consideration
|  |  | 25.4 |  | The relevant TSO may specify voltages (Ublock) at the connection points under specific network conditions whereby the HVDC system is allowed to block. Blocking means remaining connected to the network with no active and reactive power contribution for a time frame that shall be as short as technically feasible and which shall be agreed between the relevant TSOs and the HVDC system owner. | [66 empty] | Equal to Type D PPMs. | 1 - TSO internal consideration
|  |  | 25.5 |  | In accordance Article 34, undervoltage protection shall be set by the HVDC system owner to the widest possible technical capability of the HVDC converter station. The relevant system operator, in coordination with the relevant TSO, may specify narrower settings pursuant to Article 34. | [66 empty] | Equal to Type D PPMs. | 1 - TSO internal consideration
|  |  | 25.6 |  | The relevant TSO shall specify fault-ride-through capabilities in case of asymmetrical faults. | [66 empty] | Equal to symmetrical faults. | 1 - TSO internal consideration
| POST FAULT ACTIVE POWER RECOVERY |  | 26 | RTSO | The relevant TSO shall specify the magnitude and time profile of active power recovery that the HVDC system shall be capable of providing, in accordance with Article 25. | [66 empty] | Equal to Type D PPMs. | 1 - TSO internal consideration
| FAST RECOVERY FROM DC FAULTS |  | 27 |  | HVDC systems, including DC overhead lines, shall be capable of fast recovery from transient faults within the HVDC system. Details of this capability shall be subject to coordination and agreements on protection schemes and settings pursuant to Article 34. | [66 empty] | Equal to Type D PPMs. | 1 - TSO internal consideration
REQUIREMENTS FOR CONTROL | ENERGISATION AND SYNCHRONISATION OF HVDC CONVERTER STATIONS |  | 28 | RSO, RTSO | Unless otherwise instructed by the relevant system operator, during the energisation or synchronisation of an HVDC converter station to the AC network or during the connection of an energised HVDC converter station to an HVDC system, the HVDC converter station shall have the capability to limit any voltage changes to a steady-state level specified by the relevant system operator in coordination with the relevant TSO. The level specified shall not exceed 5 per cent of the pre-synchronisation voltage. The relevant system operator, in coordination with the relevant TSO, shall specify the maximum magnitude, duration and measurement window of the voltage transients. | [66 empty] | Equal to Type D PGMs. Voltage change ≤ 5% of the pre-synchronisation voltage. | 1 - TSO internal consideration
| POWER OSCILLATION DAMPING CAPABILITY |  | 30 | RTSO, HVDC SO | The HVDC system shall be capable of contributing to the damping of power oscillations in connected AC networks. The control system of the HVDC system shall not reduce the damping of power oscillations. The relevant TSO shall specify a frequency range of oscillations that the control scheme shall positively damp and the network conditions when this occurs, at least accounting for any dynamic stability assessment studies undertaken by TSOs to identify the stability limits and potential stability problems in their transmission systems. The selection of the control parameter settings shall be agreed between the relevant TSO and the HVDC system owner. | [66 empty] | Equal to Type D PGMs. | 1 - TSO internal consideration
REQUIREMENTS FOR DC-CONNECTED POWER PARK MODULES
Implementation in Member State
Aspect | Non-Exhaustive Requirement | Non-Mandatory Requirement | Article | Definition | Comment | Defined values or specifications for the requirement to be implemented | State of implementation | AT | BA | BE | BG | CH | CY | CZ | DE | DK | EE | ES | FI | FR | GB | GR | HR | HU | IE | IS | IT | LT | LU | LV | ME | MK | NL | NO | PL | PT | RO | RS | SE | SI | SK | AT |  | BA |  | BE |  | BG |  | CH |  | CY |  | CZ |  | DE |  | DK |  | EE |  | ES |  | FI |  | FR |  | GB |  | GR |  | HR
| NA |  |  | RSO/TSO | Proposal of requirements of general applications |  |  | Implementation in Member State AT: Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status | Proposal | Status
FREQUENCY STABILTY REQUIREMENTS | FREQUENCY RESPONSE |  | 39.1.a | RSO,RTSO | a DC-connected power park module shall be capable of receiving a fast signal from a connection point in the synchronous area to which frequency response is being provided, and be able to process this signal within 0,1 second from sending to completion of processing the signal for activation of the response. Frequency shall be measured at the connection point in the synchronous area to which frequency response is being provided; | [66 empty] | Exhaustive requirement. | 0 - no consideration
| FREQUENCY RANGES AND RESPONSE |  | 39.2.a | RTSO | a DC-connected power park module shall be capable of staying connected to the remote-end HVDC converter station network and operating within the frequency ranges and time periods specified in Annex VI for the 50 Hz nominal system. Where a nominal frequency other than 50 Hz, or a frequency variable by design is used, subject to agreement with the relevant TSO, the applicable frequency ranges and time periods shall be specified by the relevant TSO taking into account specificities of the system and the requirements set out in Annex VI; | [66 empty] | 47,0 Hz - 47,5 Hz: Min. 20 seconds 47,5 Hz - 49,0 Hz: Min. 90 minutes 49,0 Hz - 51,0 Hz: Unlimited 51,0 Hz - 51,5 Hz: Min. 90 minutes 51,5 Hz - 52,0 Hz: Min. 15 minutes | 1 - TSO internal consideration
| RATE-OF-CHANGE-OF-FREQUENCY |  | 39.3 |  | With regards to rate-of-change-of-frequency withstand capability, a DC-connected power park module shall be capable of staying connected to the remote-end HVDC converter station network and operable if the system frequency changes at a rate up to +/– 2 Hz/s (measured at any point in time as an average of the rate of change of frequency for the previous 1 second) at the HVDC interface point of the DC-connected power park module at the remote end HVDC converter station for the 50 Hz nominal system. | [66 empty] | Exhaustive requirement. | 0 - no consideration
| LFSM |  | 39.4 |  | DC-connected power park modules shall have limited frequency sensitive mode — overfrequency (LFSM-O) capability in accordance with Article 13(2) of Regulation (EU) 2016/631, subject to fast signal response as specified in paragraph 1 for the 50 Hz nominal system. | [66 empty] | Equal to Type D PGMs. | 1 - TSO internal consideration
|  |  | 39.5 |  | A capability for DC-connected power park modules to maintain constant power shall be determined in accordance with Article 13(3) of Regulation (EU) 2016/631 for the 50 Hz nominal system. | [66 empty] | Equal to Type D PGMs. Article 13(3) in RfG. | 1 - TSO internal consideration
|  |  | 39.6 |  | A capability for active power controllability of DC-connected power park modules shall be determined in accordance with Article 15(2)(a) of Regulation (EU) 2016/631 for the 50 Hz nominal system. Manual control shall be possible in the case that remote automatic control devices are out of service. | [66 empty] | Equal to Type D PGMs. Article 15(2)(a) in RfG. | 1 - TSO internal consideration
|  |  | 39.7 |  | A capability for limited frequency sensitive mode — underfrequency (LFSM-U) for a DC-connected power park module shall be determined in accordance with Article 15(2)(c) of Regulation (EU) 2016/631, subject to fast signal response as specified in paragraph 1 for the 50 Hz nominal system. | [66 empty] | Equal to Type D PGM (Article 15(2)(c) in RfG) | 1 - TSO internal consideration
|  |  | 39.8 |  | A capability for frequency sensitive mode for a DC-connected power park module shall be determined in accordance with Article 15(2)(d) of Regulation (EU) 2016/631, subject to a fast signal response as specified in paragraph 1 for the 50 Hz nominal system. | [66 empty] | Equal to Type D PGM (Article 15(2)(d) in RfG) | 1 - TSO internal consideration
|  |  | 39.9 |  | A capability for frequency restoration for a DC-connected power park module shall be determined in accordance with Article 15(2)(e) of Regulation (EU) 2016/631 for the 50 Hz nominal system. | [66 empty] | Equal to Type D PGM (Article 15(2)(e) in RfG) | 1 - TSO internal consideration
|  |  | 39.10 |  | Where a constant nominal frequency other than 50 Hz, a frequency variable by design or a DC system voltage is used, subject to the agreement of the relevant TSO, the capabilities listed in paragraphs 3 to 9 and the parameters associated with such capabilities shall be specified by the relevant TSO. | [66 empty] | Site specific requirement. | 1 - TSO internal consideration
VOLTAGE RELATED PARAMETERS | VOLTAGE RANGE |  | 40.1.a |  | a DC-connected power park module shall be capable of staying connected to the remote-end HVDC converter station network and operating within the voltage ranges (per unit), for the time periods specified in Tables 9 and 10, Annex VII. The applicable voltage range and time periods specified are selected based on the reference 1 pu voltage; | [66 empty] | 110 kV ≤ Un < 300 kV 0,85 pu - 0,90 pu: Min. 60 minutes 0,90 pu - 1,10 pu: Unlimited 1,10 pu - 1,118 pu: Unlimited 1,118 pu - 1,15 pu: Min. 60 minutes 300 kV < Un ≤ 400 kV 0,85 pu - 0,90 pu: Min. 60 minutes 0,90 pu - 1,05 pu: Unlimited 1,05 pu - 1,15 pu: Min. 60 minutes | 1 - TSO internal consideration
|  |  | 40.1.d |  | for HVDC interface points at AC voltages that are not included in the scope of Annex VII, the relevant system operator, in coordination with the relevant TSO shall specify applicable requirements at the connection point; | [66 empty] | Site specific requirement. | 1 - TSO internal consideration
|  |  | 40.1.e |  | where frequencies other than nominal 50 Hz are used, subject to relevant TSO agreement, the voltage ranges and time periods specified by the relevant system operator, in coordination with the relevant TSO, shall be proportional to those in Tables 9 and 10, Annex VII. | [66 empty] | Proportional to values in Annex VII (Table 9 and Table 10). | 1 - TSO internal consideration
| REACTIVE POWER CAPABILITY |  | 40.2.b.i |  | DC-connected power park modules shall fulfil the following requirements relating to voltage stability either at the time of connection or subsequently, according to the agreement as referred to in point (a): (i) with regard to reactive power capability at maximum HVDC active power transmission capacity, DC-connected power park modules shall meet the reactive power provision capability requirements specified by the relevant system operator, in coordination with the relevant TSO, in the context of varying voltage. The relevant system operator shall specify a U-Q/Pmax-profile that may take any shape with ranges in accordance with Table 11, Annex VII, within which the DC-connected power park module shall be capable of providing reactive power at its maximum HVDC active power transmission capacity. The relevant system operator, in coordination with the relevant TSO, shall consider the long term development of the network when determining these ranges, as well as the potential costs for power park modules of delivering the capability of providing reactive power production at high voltages and reactive power consumption at low voltages. | [66 empty] | U-Q/P profile according to Annex VII Table 11. Range of width of Q/Pmax profile: 0 - 0,95 Range of steady-state voltage level: 0,1 pu - 0,225 pu | 1 - TSO internal consideration
OTHER ASPECTS | CONTROL REQUIREMENTS |  | 41.1 |  | During the synchronisation of a DC-connected power park module to the AC collection network, the DC- connected power park module shall have the capability to limit any voltage changes to a steady-state level specified by the relevant system operator, in coordination with the relevant TSO. The level specified shall not exceed 5 per cent of the pre-synchronisation voltage. The relevant system operator, in coordination with the relevant TSO, shall specify the maximum magnitude, duration and measurement window of the voltage transients. | [66 empty] | Equal to Type D PGMs. Voltage change ≤ 5% of the pre-synchronisation voltage. | 1 - TSO internal consideration
|  |  | 41.2 |  | The DC-connected power park module owner shall provide output signals as specified by the relevant system operator, in coordination with the relevant TSO. | [66 empty] | Equal to Type D PGMs. | 1 - TSO internal consideration
| NETWORK CHARACTERISTIC |  | 42 |  | With regard to the network characteristics, the following shall apply for the DC-connected power park modules: (a) each relevant system operator shall specify and make publicly available the method and the pre-fault and post-fault conditions for the calculation of minimum and maximum short circuit power at the HVDC interface point; (b) the DC-connected power park module shall be capable of stable operation within the minimum to maximum range of short circuit power and network characteristics of the HVDC interface point specified by the relevant system operator, in coordination with the relevant TSO; (c) each relevant system operator and HVDC system owner shall provide the DC-connected power park module owner with network equivalents representing the system, enabling the DC-connected power park module owners to design their system with regard to harmonics; 8.9.2016 L 241/23 Official Journal of the European Union EN | [66 empty] | Equal to NC HVDC (Article 32), Equal to Type D PGMs. | 1 - TSO internal consideration
| POWER QUALITY |  | 44 |  | DC-connected power park modules owners shall ensure that their connection to the network does not result in a level of distortion or fluctuation of the supply voltage on the network, at the connection point, exceeding the level specified by the relevant system operator, in coordination with the relevant TSO. The necessary contribution from grid users to associated studies, including, but not limited to, existing DC-connected power park modules and existing HVDC systems, shall not be unreasonably withheld. The process for necessary studies to be conducted and relevant data to be provided by all grid users involved, as well as mitigating actions identified and implemented, shall be in accordance with the process in Article 29. | [66 empty] | Equal to Type D PGMs. | 1 - TSO internal consideration
| GENERAL SYSTEM MANAGEMENT REQUIREMENTS APPLICABLE TO DC-CONNECTED POWER PARK MODULES |  | 45 |  | With regard to general system management requirements, Articles 14(5), 15(6) and 16(4) of Regulation (EU) 2016/631 shall apply to any DC-connected power park module. | [66 empty] | Equal to Type D PGMs. | 1 - TSO internal consideration
REQUIREMENTS FOR REMOTE-END HVDC CONVERTER STATIONS
Aspect | Non-Exhaustive Requirement | Non-Mandatory Requirement | Article | Definition | Comment | Defined values or specifications for the requirement to be implemented | State of implementation | AT | BA | BE | BG | CH | CY | CZ | DE | DK | EE | ES | FI | FR | GB | GR | HR | HU | IE | IS | IT | LT | LU | LV | ME | MK | NL | NO | PL | PT | RO | RS | SE | SI | SK
| NA |  | 5.4 | RSO/TSO | Proposal of requirements of general applications
Note on G61: It should be indicated if the proposal has been submitted and when (in order to verifiy the compliance within the 2 years)
Note on G95: It should be indicated if the proposal has been submitted and when (in order to verifiy the compliance within the 2 years)

## Parameters (hidden)
0 - no consideration
1 - TSO internal consideration
2a - preliminary: shared with stakeholders, but not publicly available
2b - preliminary: shared with stakeholders and publicly available
3 - selected for approval
4 - approved/binding